|  |  |  | NYS STATEMENT OF SPECIAL INSPECTIONS Required by the Building Code of New York State (BCNYS) |  |
| --- | --- | --- | --- | --- |
| BCNYS §1705.1 requires that the project Registered Design Professional in responsible charge prepare a Statement of Special Inspections. Completion of this Statement of Special Inspections and submission to the Code Compliance Unit with the Construction Permit Application is a condition for issuance of the Construction Permit. This Statement shall also be bound in the project manual in accordance with General Requirements Section 014000. |  |  |  |  |
| Campus/Facility: |  |  |  |  |
| Project Title: |  |  |  |  |
| Project #: |  | DASNY Project Manager: |  |  |
| Registered Design Professional (RDP): |  |  |  |  |
| Name of Person Completing Statement: |  |  | Phone: | Date: |
| Comments: |  |  |  |  |

| INSPECTIONS AND TESTS (Continuous & Periodic is as defined by the BCNYS) | CONTINUOUS | PERIODIC | BCNYS REFERENCE | CHECK IF REQUIRED | SPECIFICATION REFERENCE AND CLARIFYING NOTES (by RDP)1 | COMMENTARY/NOTES (by DASNY)2 |
| --- | --- | --- | --- | --- | --- | --- |
| ## A. Inspection of Fabricators |  |  | 1704.2 1704.2.1 1704.2.2 |  |  | Review qualifications of fabricators and verify accreditations. Perform in- plant review where required, or as specified on the documents. |
| ## 1. Structural Steel |  |  | 1704.2, 1704.3, Table 1704.3 |  |  |  |
| ## 2. Steel Joists |  |  | 1704.2 |  |  |  |
| ## 3. Precast Concrete |  |  | 1704.2, 1704.4, Table 1704.4 |  |  |  |
| ## 4. Wood Construction |  |  | 1704.2, 1704.6 |  |  |  |
| ## B. Steel Construction |  |  | 1704.3 |  |  |  |
| 1. Material verification of high-strength bolts, nuts, and washers: |  |  | Table 1704.3 |  |  | Includes submittal review and field verification. |
| a. Identification markings conform to ASTM standards specified in the approved construction documents |  | X |  |  |  |  |
| b. Manufacturer’s certificate of compliance required. |  | X |  |  |  |  |
| 2. Inspection of high-strength bolting: |  |  | Table 1704.3, 1704.3.3 |  |  | Field inspection |
| a. Bearing type connection |  | X |  |  |  |  |
| b. Slip critical type connection | X |  |  |  |  |  |
| 3. Material verification of structural steel: |  |  | Table 1704.3 |  |  |  |
| a. Identification of markings |  | X |  |  |  | Field inspection. Assure conformance to ASTM standards specified in the approved documents. |
| b. Certified mill test reports |  | X |  |  |  | Review each submittal. |
| 4. Material verification of weld filler materials |  | X | Table 1704.3 |  |  | Includes (a) review of manufacturer’s certificate of compliance and (b) field verification of identification markings to AWS specification. |
| 5. Structural steel welding: |  |  | Table 1704.3 1704.3.1 |  |  | Shop and field inspection. Non-destructive testing requirements and frequencies as specified in the contract documents. |
| a. Complete and partial penetration groove welds. | X |  |  |  |  |  |
| b. Multi-pass fillet welds | X |  |  |  |  |  |
| c. Single pass fillet welds >5/16” | X |  |  |  |  |  |
| d. Single pass fillet welds ≤ 5/16”, floor and deck welds |  | X |  |  |  |  |
| e. Floor and roof deck welds |  | X |  |  |  |  |
| 6. Reinforcing steel welding: |  |  | Table 1704.3, 1704.3.1 |  |  | Shop and field inspections. |
| a. Verification of weldability of steel other than ASTM A706 |  | X |  |  |  |  |
| b. Reinforcing steel-resisting flexural and axial forces | X |  |  |  |  |  |
| c. Shear reinforcement | X |  |  |  |  |  |
| d. Other reinforcing steel |  | X |  |  |  |  |
| 7. Inspection of steel frame joint details for compliance with approved construction documents: |  |  | 1704.3.2, Table 1704.3 |  |  | Field inspection. |
| a. Details such as bracing and stiffening. |  | X |  |  |  |  |
| b. Member locations |  | X |  |  |  |  |
| c. Application of joint details at each connection. |  | X |  |  |  |  |
| ## C. Concrete Construction |  |  | 1704.4 |  |  |  |
| 1. Inspection of reinforcing steel and placement. |  | X | Table 1704.4 |  |  | Field inspection. |
| 2. Inspection of pre-stressing tendons and placement. |  | X | Table 1704.4 |  |  | In plant or field review. |
| 3. Inspection of reinforcing steel welding in accordance w/ item 6b above. |  | X | Table 1704.4, 1704.4.1 |  |  | Includes anchor bolt welding. |
| 4. Inspection of bolts to be installed in cast-in-place concrete prior to and during placement. | X |  | Table 1704.4 |  |  | Field inspection. |
| 5. Verify use of required design mix and evaluation and acceptance of concrete and shotcrete. |  | X | Table 1704.4 |  |  | Submittal review. Batch plant inspection as specified in the contract documents. |
| 6. Sampling fresh concrete: slump, air content, temperature, strength test specimens. | X |  | Table 1704.4 |  |  | Includes all field testing and evaluation of laboratory strength reports. Frequency of sampling and testing must be per the contract documents. |
| 7. Inspection of concrete placement for proper application techniques. | X |  | Table 1704.4 |  |  | Also includes precast and shotcrete placement. For precast inspection (in-plant) specify PCI-MNL116 |
| 8. Inspection for maintenance of specified curing temperature and techniques. |  | X | Table 1704.4 |  |  | Field inspection of curing process. |
| 9. Inspection of prestressed concrete: |  |  | Table 1704.4, 1704.2 |  |  | In plant or field review required. |
| a. Application of pre-stressing forces | X |  |  |  |  |  |
| b. Grouting of bonded pre-stressing tendons in the seismic-force-resisting system. | X |  |  |  |  |  |
| 10. Erection of precast concrete members. |  | X | Table 1704.4 |  |  | Specify PCI-MNL127. |
| 11. Verification of in-situ concrete strength prior to stressing of tendons in post tensioned concrete and prior to removal of shores and forms from beams and structural slabs. |  | X | Table 1704.4 |  |  | Review field testing and laboratory reports. |
| 12. Inspect formwork for shape, location and dimensions of the concrete member being formed. |  | X | Table 1704.4 |  |  |  |
| ## D. Masonry Construction ## (Check L1 or L2 below) L1 = Level 1 Inspection L2 = Level 2 Inspection |  |  | 1704.5 Tables 1704.5.1 & 1704.5.3 |  |  | See BCNYS 1704.5 for clarification of Level 1 vs. Level 2 inspection. |
| 1. Verify the following to ensure compliance: |  |  | Tables 1704.5.1 & 1704.5.3 |  |  |  |
| a. Proportions of site prepared mortar and grout |  | X L1L2 |  |  |  | Submittal review and field verification. |
| b. Verify placement of masonry units and construction of mortar joints. |  | X L1L2 |  |  |  | Field inspection. |
| c. Location and placement of reinforcement, connectors, tendons, anchorages. |  | X L1 L2 |  |  |  | Field inspection. |
| d. Pre-stressing technique and tendon installation. |  | X L1 L2 |  |  |  |  |
| e. Grade and size of tendons and anchorages. |  | X L1 |  |  |  |  |
| f. Grout specs prior to grouting. | X L2 |  |  |  |  |  |
| g. Grouting of prestressed bonded tendons. | X L1 L2 |  |  |  |  |  |
| 2. Inspection program shall verify: |  |  | Tables 1704.5.1 & 1704.5.3 |  |  |  |
| a. Size and location of structural masonry elements & workmanship. |  | X L1L2 |  |  |  | Field and submittal review. |
| b. Type, size and location of anchors, including other details of anchorage of masonry to structural members, frames or other. | X L2 | X L1 |  |  |  | Field inspection. |
| c. Specified size, grade and type of reinforcement. |  | X L1L2 |  |  |  | Field inspection. |
| d. Welding of reinforcing bars. | X L1L2 |  |  |  |  | Field inspection. |
| e. Cold/hot weather protection of masonry construction. |  | X L1L2 |  |  |  | Field inspection. |
| f. Pre-stressing force measurement and application. | X L2 | X L1 |  |  |  | Field inspection. |
| 3. Verify grout space is clean prior to grouting. | X L2 | X L1 | Tables 1704.5.1 & 1704.5.3 |  |  | Field inspection. |
| 4. Verify grout placement complies with BCNYS and construction document provisions. | X L1 L2 |  | Tables 1704.5.1, 1704.5.3 |  |  | Grout placement shall be verified to ensure compliance with Code and construction document provisions. |
| 5. Preparation of grout specimens, mortar specimens and prisms. | X L1 L2 |  | Tables 1704.5.1 & 1704.5.3 |  |  | Includes observation of contractors sampling and preparation of samples by the Special Inspection agent. |
| 6. Verify compliance with inspection provisions of Construction Documents and approved submittals. |  | X L1L2 | Tables 1704.5.1 & 1704.5.3 |  |  | Inspection and test requirements per the contract documents. Inspection(s) may need to be continuous. |
| E. Wood Construction: |  |  | 1704.6 |  |  |  |
| 1. High-load diaphragms. |  | X | 1704.6.1 |  |  | Inspection of wood structural panel sheathing and size of framing members at adjoining panel edges, including fastening details. |
| ## F. Soils |  |  | 1704.7 |  |  |  |
| ## 1. Foundation subgrades | X |  | 1704.7 Table 1704.7 |  |  | All subgrades for buildings must be observed and verified prior to being covered by controlled fill or otherwise obscured by the placement of forms, reinforcing steel or concrete. |
| 2. Site preparation. |  | X | 1704.7.1 Table 1704.7 |  |  | Field inspection and testing to verify that the site is prepared in accordance with the approved soils report (1802.2). |
| 3. During fill placement. | X |  | 1704.7.2 Table 1704.7 |  |  | Review submittals, field testing and inspection. Verify soil types and lift thickness are per contract documents. |
| 4. Evaluation of in-place density. | X |  | 1704.7.3 Table 1704.7 |  |  | Field testing. Verify conformance with contract documents. |
| G. Pile Foundations: Installation and load tests. | X |  | 1704.8 Table 1704.8 |  |  | Includes monitoring the installation of test piles, load testing, production pile installation and the review of pile survey. |
| H. Pier Foundations: | X |  | 1704.9 Table 1704.9 |  |  | Includes full time observation of drilling operations. |
| ## I. Sprayed Fire-Resistant Materials |  |  | 1704.10 |  |  |  |
| 1. Structural member surface conditions. |  | X | 1704.10.1 |  |  | Field review of surface conditions prior to application. |
| 2. Application. |  | X | 1704.10.2 |  |  | Field review during application. |
| 3. Thickness. |  | X | 1704.10.3 |  |  | Field test. |
| 4. Density. |  | X | 1704.10.4 |  |  | Collect field sample, test in laboratory. |
| 5. Bond strength. |  | X | 1704.10.5 |  |  | Field test. |
| J. Mastic and Intumescent Fire-Resistant Coatings |  | X | 1704.11 |  |  | Provide in accordance with AWCI Manual 12-B. |
| K. Exterior Insulation and Finish Systems (EIFS) |  | X | 1704.12 |  |  | Field review of application/ installation. |
| ## L. Special Cases |  |  | 1704.13 |  |  | Applies to alternative materials and systems, when requested by A/E or Building Official. Review system & installation. |
| ## M. Smoke Control |  | X | 1704.14 |  |  | Inspect during ductwork, erection and system testing. Inspect prior to covering (enclosing). |
| ## N. Special Inspections for Seismic Resistance |  |  | 1705.3 1705.3.1 1707 | Provide additional details of required inspections and tests for seismic resistance under Part R of this form as necessary. Note SDC = Seismic Design Category. |  |  |
| 1. Seismic-force-resisting systems | X | X | 1705.3(1) 1707.2 1707.3 1707.4 |  |  | SDC C, D, E or F |
| 2. Designated seismic systems | X | X | 1707.3(2) 1707.9 1708.5 |  |  | SDC D, E or F |
| 3. Mechanical and electrical components |  |  | 1705.3(3) 1705.3(5) |  |  |  |
| - Anchorage of electrical equip. for emergency / stand-by power |  | X | 1707.8(1) |  |  | SDC C, D, E or F |
| - Anchorage of other electrical equipment |  | X | 1707.8(2) |  |  | SDC E or F |
| - Piping systems carrying flammable, combustible or toxic contents |  | X | 1707.8(3) |  |  | SDC C, D, E or F |
| - HVAC ductwork containing hazardous materials |  | X | 1707.8(4) |  |  | SDC C, D, E or F |
| - Vibration isolation systems* |  | X | 1707.8(5) |  |  | SDC C, D, E or F * applies only in certain applications, refer to 1707.8(5) |
| 4. Storage racks, access floors and architectural components |  | X | 1705.3(4) 1707.6 1707.7 |  |  | SDC D, E or F |
| 5. Seismic isolation system. |  | X | 1707.10 |  |  |  |
| ## O. Special Inspections for Wind Resistance: |  |  | 1705.4 | Provide additional details of required inspections and tests for wind resistance under Part R of this form as necessary. |  |  |
| 1. Roof cladding and roof framing connections.. |  |  | 1705.4.2.1 |  |  |  |
| 2. Wall connections to roof and floor diaphragms and framing. |  |  | 1705.4.2.2 |  |  |  |
| 3. Roof and floor diaphragm systems. |  |  | 1705.4.2.3 |  |  |  |
| 4. Vertical windforce-resisting systems. |  |  | 1705.4.2.4 |  |  |  |
| 5. Windforce-resisting system connections to the foundation. |  |  | 1705.4.2.5 |  |  |  |
| 6. Systems or components required to meet impact-resistance requirements. |  |  | 1705.4.2.6 |  |  |  |
| ## P. Structural Testing for Seismic Resistance: |  | X | 1708 |  |  |  |
| 1. Testing and verification of masonry materials and assemblies. |  | X | 1708.1 |  |  | Requirements depend on the classification of the structure or nature of occupancy. |
| 2. Reinforcing and Prestressing steel. |  |  | 1708.2 1708.3 |  |  | Requirement depends on Seismic Design Category. |
| 3. Structural steel. |  |  | 1708.2 1708.4 |  |  | Requirement depends on Seismic Design Category. |
| 4. Seismic qualification of mechanical and electrical equipment. |  |  | 1708.2 1708.5 |  |  | Requirement depends on Seismic Design Category. |
| Q. Structural Observations: |  |  | 1709 |  |  | Requirements depend on the classification of the structure or nature of occupancy. |
| ## 1. For seismic resistance |  |  | 1709.2 |  |  | Refer to BC 1709.2 for applicability. |
| ## 2. For wind requirements |  |  | 1709.3 |  |  | Refer to BC 1709.3 for applicability. |
| ## R. Additional Special Inspections/Tests |  |  | The registered design professional of record shall identify if additional tests and inspections defined by BC 1707 through 1715 are required and provide specific requirements below. |  |  |  |

NOTES:

- RDP to provide reference specification section detailing the requirements for inspections and/or tests and other clarifying notes, as necessary.

- Commentary/Notes by DASNY are provided for information only and are not intended to provide complete details of the required tests and inspections.  Refer to the Building Code of New York State for complete and detailed requirements.