# FIRESTOPPING SPECIFICATION

SECTION 078400 - FIRESTOPPING

## PART 1 – GENERAL

- RELATED DOCUMENTS

  - Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

- SUMMARY

  - Provide firestop systems consisting of a material, or combination of materials installed to retain the integrity of fire resistance rated construction by maintaining an effective barrier against the spread of flame, smoke and/or hot gases through penetrations, fire resistive joints, and perimeter openings in accordance with the requirements of the Building Code, Life Safety Code, or other reference standard applicable to this project.

  - Firestop systems shall be used in locations including, but not limited to, the following:

    - Penetrations through fire resistance rated floor and roof assemblies including both empty openings and openings containing penetrants.

    - Penetrations through fire resistance rated wall assemblies including both empty openings and openings containing penetrants.

    - Membrane penetrations in fire resistance rated wall, floor, floor-ceiling, or roof-ceiling assemblies where items penetrate one side of such assembly.

    - Joints between fire resistance rated assemblies.

    - Perimeter gaps between rated floors/roofs and an exterior wall assembly.

  - Related Sections include, but are not limited to, the following:

    - Division 07 – Thermal and Moisture Protection

    - Division 09 – Finishes

    - Division 21 – Fire Suppression

    - Division 22 – Plumbing

    - Division 23 – Heating, Ventilating and Air Conditioning

    - Division 25 – Automation

    - Division 26 – Electrical

    - Division 27 – Communications

    - Division 28 – Electrical Safety and Security

- REFERENCES

  - New York State Uniform Fire Prevention and Building Code, New York City Construction Codes, or the applicable code effective in the jurisdiction.

  - National Fire Protection Association (NFPA)

    - NFPA 101 (Life Safety Code)

  - American Society For Testing and Materials Standards (ASTM):

    - ASTM E84:	Standard Test Method for Surface Burning Characteristics of Building Materials.

    - ASTM E814:	Standard Test Method for Fire Tests of Through-Penetration Firestops.

    - ASTM E1966:	Test Method for Resistance of Building Joint Systems.

    - ASTM E1399:	Test Method for Cyclic Movement and Measuring Minimum and Maximum Joint Width.

    - ASTM E119:	Methods of Fire Tests of Building Construction and Materials.

    - ASTM E2174:	Standard Practice for On-Site Inspection of Installed Fire Stops.

    - ASTM E2307:	Standard Test Method for Determining the Fire Endurance of Perimeter Fire Barrier Systems Using the Intermediate-Scale, Multi Story Test Apparatus (ISMA).

    - ASTM E2393: 	Standard Practice for On-Site Inspection of Installed Fire Resistive Joint Systems and Perimeter Fire Barriers.

  - Underwriters Laboratories Inc. (UL):

    - UL Qualified Firestop Contractor Program.

    - UL 263:	Fire Tests of Building Construction and Materials.

    - UL 723:	Surface Burning Characteristics of Building Materials.

    - UL 1479:	Fire Tests of Through-Penetration Fire Stops.

    - UL 2079:	Tests for Fire Resistance of Building Joint Systems.

  - UL Fire Resistance Directory:

    - Through-Penetration Firestop Devices (XHJI)

    - Fire Resistive Ratings (BXUV)

    - Through-Penetration Firestop Systems (XHEZ)

    - Fill, Void, or Cavity Material (XHHW)

  - Intertek Group plc.:

    - Directory of Listed Building Products

  - Factory Mutual Research (FM):

    - FM 4991:	FM Approval Standard for Firestop Contractors – Class 4991

- DEFINITIONS

  - Firestopping: The use of a material or combination of materials in a fire-resistance-rated assembly where it has been breached, so as to maintain the integrity of the fire rating.

  - System: An assembly that is tested and listed by an Approved Testing Agency that is used to protect penetration(s) of fire-resistance-rated assemblies, and can consist of one or more of the following components: a specific firestop material, combination of materials, or firestop device(s), in conjunction with wall or horizontal assembly construction, a specific penetrant(s), and minimum and maximum annular space.

  - Fire-resistance-rated Assembly: Wall, floor, roof, floor-ceiling, or roof-ceiling construction designed to have the ability to confine a fire, continue to perform a given structural function, or both, for a period of time as determined by the tests or the methods prescribed by the Building Code.

  - Through-penetration: A breach in both sides of a floor, floor-ceiling, or wall assembly to accommodate an item passing through the breaches.

  - Through-penetration Firestop System: An assemblage consisting of a fire-resistance-rated floor, floor-ceiling, or wall assembly, one or more penetrating items passing through the breaches in both sides of the assembly and the materials or devices, or both, installed to resist the spread of fire through the assembly for a prescribed period of time.

  - Membrane-penetration: A breach in one side of a floor-ceiling, roof-ceiling or wall assembly to accommodate an item installed into or passing through the breach.

  - Membrane-penetration Firestop: A material, device or construction installed to resist for a prescribed time period the passage of flame and heat through openings in a protective membrane in order to accommodate cables, cable trays, conduit, tubing, pipes or similar items.

  - Membrane-Penetration Firestop System: An assemblage consisting of a fire-resistance-rated floor, floor-ceiling, roof-ceiling or wall assembly, one or more penetrating items installed into or passing through the breach in one side of the assembly and the materials or devices, or both, installed to resist the spread of fire into the assembly for a prescribed period of time.

  - Joint: The opening in or between adjacent assemblies that is created due to building tolerances, or is designed to allow independent movement of the building in any plane caused by thermal, seismic, wind or any other loading. Joints also include gaps between rated assemblies of dissimilar materials.

  - Fire-resistant Joint System: An assemblage of specific materials or products that are designed, tested and fire-resistance rated in accordance with either ASTM E1966 or UL 2079 to resist for a prescribed period of time the passage of fire through joints made in or between fire-resistance-rated assemblies.

  - F Rating: The time period that the through-penetration firestop system limits the spread of fire through the penetration when tested in accordance with ASTM E814 or UL 1479.

  - T Rating: The time period that the penetration firestop system, including the penetrating item, limits the maximum temperature rise to 325 ºF (163 ºC) above its initial temperature through the penetration on the nonfire side when tested in accordance with ASTM E814 or UL 1479.

  - Smoke Barrier: A continuous membrane, either vertical or horizontal, such as a wall, floor or ceiling assembly, that is designed and constructed to restrict the movement of smoke.

  - Approved Testing Agencies: Include but not limited to: Underwriters Laboratory (UL), Factory Mutual (FM), Warnock Hersey, and Intertek Group plc.

- PERFORMANCE REQUIREMENTS

  - Penetrations: Provide through-penetration and membrane-penetration firestop systems that are produced and installed to resist the spread of fire, passage of smoke and other hot gases according to requirements indicated, to restore the original fire-resistance rating of assembly penetrated.

    - Provide and install complete penetration firestopping systems that have been tested and approved by nationally accepted testing agencies per ASTM E814 or UL 1479 fire tests in a configuration that is representative of field conditions.

    - F-Rated Systems:  Provide firestop systems with F-ratings indicated, as determined per ASTM E814 or UL 1479, but not less than one (1) hour or the fire resistance rating of the assembly being penetrated.

    - T-Rated Systems: Provide firestop systems with T-ratings indicated, as well as F-ratings, as determined per ASTM E814 or UL 1479, and where required by the Building Code for floor penetrations which are not located within the cavity of a wall above or below the floor, or the concealed space of a fire-resistance-rated horizontal assembly.

    - L- Rated Systems: Provide firestop systems with L- ratings less than 5cfm/sf at smoke barriers.

    - W-Rated systems: Provide firestop systems that are resistant to water. For piping penetrations for plumbing and wet-pipe sprinkler systems, provide moisture-resistant through-penetration firestop systems.

    - For penetrations involving non-metallic, CPVC, PVC, or plastic piping, tubing or conduit, provide firestop systems that are chemically compatible in accordance with Manufacturer requirements.

    - For penetrations involving fire or fire/smoke dampers, only firestop products approved by the damper manufacturer shall be installed in accordance with the damper installation instructions.

  - Fire Resistive Joints: Provide joint systems with fire resistance assembly ratings indicated, as determined by UL 2079 or ASTM E1966, but not less than the fire resistance assembly rating of the construction in which the joint occurs. Firestopping assemblies must be capable of withstanding anticipated movements for the installed field conditions.

    - For firestopping assemblies exposed to view, traffic, moisture, and physical damage, provide products that after curing do not deteriorate when exposed to these conditions both during and after construction.

    - For floor penetrations exposed to possible loading and traffic, provide firestop systems capable of supporting floor loads involved either by installing floor plates or by other means, as specified by the Architect.

    - L- Rated Systems: Provide firestop systems with L- ratings less than 5cfm/sf at smoke barriers.

  - Firestopping products shall have flame spread ratings less than 25 and smoke-developed ratings less than 450, as determined per ASTM E 84. Note: Firestop products installed in plenum spaces shall have a smoke developed rating less than 50.

  - Engineering Judgment (EJ): Where there is no specific third party tested and classified firestop system available for an installed condition, the Contractor shall obtain from the firestopping material manufacturer an Engineering Judgment (EJ) to be submitted to the Design Professional and where required the Authority Having Jurisdiction for approval prior to installation. The EJ shall follow International Firestop Council (IFC) guidelines. Note: Tested and Listed firestop systems are to be used before an Engineering Judgment (EJ).  Engineering Judgments (EJ) shall not be utilized as an alternative to proper construction or coordination.

- SUBMITTALS

  - Product Data: For each type of firestopping product selected. Manufacturer certification must verify that firestopping materials are free of asbestos, lead and contain volatile organic compounds (VOCs) within limits of NYS requirements.

  - Design Listings: Submit system design listings, including illustrations, from a qualified testing and inspecting agency that is applicable to each firestop configuration. Systems shall be representative of the conditions present in the field.

  - Installation Instructions: Submit the manufacturer’s installation instruction for each firestop assembly.

  - Where there is no specific third party tested and classified firestop system available for a particular configuration, the Contractor shall obtain from the firestopping material manufacturer an Engineering Judgment (EJ) for submittal.

  - Safety Data Sheet (SDS): Submit for each type of firestopping product selected.

  - Qualification Data: For firms and persons specified in “Quality Assurance” Article to demonstrate their capabilities and experience. Submit documents as per 1.7.

  - A quality control manual approved by FM or UL (if applicable).

  - Firestop Schedule: Submit schedule (see Appendix A) itemizing the following:

    - Manufacturer’s product reference numbers and/or drawing numbers.

    - Listing agency’s design number.

    - Penetrating Item Description/Limits: Material, size, insulated or uninsulated, and combustibility.

    - Maximum allowable annular space or maximum size opening.

    - Wall type construction.

    - Floor, roof, floor-ceiling, or roof-ceiling type construction.

    - Hourly fire-resistance rating of wall, floor, floor-ceiling, or roof-ceiling assembly.

    - F rating.

    - T rating, if applicable.

    - L and W rating, if applicable.

  - Firestop Application Log: A separate binder shall be prepared and kept on site for use by the Inspection Agency, the Authority Having Jurisdiction, and any other parties responsible for reviewing installations. The binder shall contain the following:

    - The binder shall be a three (3) ring binder.

    - Firestop Schedule (see appendix A).

    - All approved firestopping assemblies including Engineering Judgments shall be provided and organized by trade.

    - Copy of manufacturer’s installation instruction for each firestop assembly.

    - A matrix or table of contents listing each assembly shall be provided.

    - The binder shall be updated as new firestop assemblies or EJ’s are added.

    - The binder shall be kept on-site at a location approved by the Owner.

    - Qualifications or Certification of each Installer.

    - A copy of floor plans showing locations and rating of fire-resistance rated assemblies.

- QUALITY ASSURANCE

  - Provide firestopping system design listings from UL, FM, Warnock Hersey or Intertek in accordance with the appropriate ASTM Standard(s) per article 1.5.

  - Contractor Qualifications: An acceptable Firestop Contractor shall be:

    - FM Research approved in accordance with FM Standard 4991, or

    - UL Qualified Firestop Contractor, or

    - Meet the following requirements:

      - Installation personnel shall be trained by the approved firestop manufacturer,

      - The installation firm shall be experienced in installing firestop systems and fire resistive joint systems similar in material, design, and extent to that indicated for this Project, whose work has resulted in construction with a record of successful performance, and

      - Qualifications include having the necessary experience, staff, and training to install manufacturer's products per specified tested and listed system requirements.

  - Single Source Limitations: Obtain firestop systems for all conditions from a single manufacturer. The only exception is where a listed firestop system is available for a specific opening from another manufacturer, it shall be utilized before an Engineering Judgment.

  - Materials from different firestop manufacturers shall not be installed in the same firestop system or opening.

  - Firestopping materials shall not shrink upon drying as evidenced by cracking or pulling back from contact surfaces such that a void is created. Where shrinking is observed the firestop system shall be corrected in accordance with the system’s listing.

  - Materials used shall be installed in accordance with the manufacturer’s written installation instructions.

  - Identify installed firestop systems with preprinted metal, plastic, or laminated paper labels. Attach labels permanently to surfaces adjacent to and within 6 inches (150 mm) of edge of the firestop systems so that labels will be visible to anyone seeking to remove penetrating items or firestop systems. In addition, for perimeter or joint firestop systems attach labels at locations every 20 feet or at least each section where separated. Use mechanical fasteners for metal labels. For plastic and laminated paper labels, use self-adhering type with adhesives capable of permanently bonding labels to surfaces on which labels are placed and provide a label material that will result in partial destruction of label if removal is attempted. Include the following information on labels:

    - The words "Warning - Firestop System - Do Not Disturb. Notify Building Management of Any Damage."

    - Contractor's name, address, and phone number.

    - Firestop system designation of applicable testing and listing agency.

    - Date of installation.

    - Firestop system manufacturer's name.

    - Installer's name.

    - Inspector’s name (if applicable).

    - Labels with scannable QR codes that direct to online versions of the firestop system shall be acceptable so long as all items listed between #1-7 are addressed by the label and the manufacturer’s website.

  - Inspection of penetrations through fire rated floor, floor-ceiling, roof-ceiling and wall assemblies shall be in accordance with ASTM E2174, Standard Practice for On-Site Inspection of Installed Fire Stops. Inspection of joint systems between rated assemblies shall be in accordance with ASTM E2393, Standard Practice for On-Site Inspection of Installed Fire Resistive Joint Systems and Perimeter Fire Barriers. The Owner may engage a qualified independent inspection agency or material testing agency to perform these inspections. Where one of the following conditions occur, the Owner shall engage a qualified independent inspection agency.

    - NYC Projects are subject to the requirements of Special Inspections in accordance with Chapter 17 of the NYC Construction Codes.

    - NYS Projects are subject to the requirements of Special Inspections in accordance with Chapter 17 of the Building Code of NYS, for high-rise buildings or in buildings assigned to Risk Category III or IV.

  - Field Mock-up Installations: Prior to installing firestop systems, erect mock-up installations for each type of firestop or fire-resistant joint system indicated in the Firestop Schedule to verify selections made and to establish standard of quality and performance by which the firestopping work will be judged by the Owner or Owner’s Representative. Obtain acceptance of mock-up installations by the Owner or Owner’s Representative before start of subsequent firestop system installation. Provide at least 72 hours’ notice to Owner or Owner’s Representative prior to inspection.

- DELIVERY, STORAGE, AND HANDLING

  - Deliver firestopping products to Project site in original, unopened containers or packages with intact and legible manufacturer’s labels identifying product and manufacturer, date of manufacture/expiration, lot number, listing agency’s classification marking, and mixing instructions for multi-component materials.

  - Store and handle materials per manufacturer’s instructions to prevent deterioration or damage due to moisture, temperature changes, contaminants, or other causes.

  - All firestop materials shall be installed prior to expiration date.

- PROJECT CONDITIONS

  - Environmental Limitations: Install firestopping when ambient or substrate temperatures are within limits permitted by the manufacturer’s written instructions. Do not install firestopping when substrates are wet due to rain, frost, condensation, or other causes.

  - Ventilate per the manufacturers written instructions on the product’s Safety Data Sheet.

  - Verify the condition of the substrates before starting work.

  - Care should be taken to ensure that firestopping materials are installed so as not to contaminate adjacent surfaces.

- COORDINATION

  - Preinstallation Conference: This conference shall be a joint meeting attended by the Owner’s Representative and all prime contractors, respective firestopping sub-contractors and firestopping company field advisor to review project requirements.  The agenda for the conference should include the following topics:

- Review scope of work.

- Review shop drawings and firestop application log.

- Review mock-up requirements.

- Discuss identification labels and locations.

- Review schedule, coordination and sequencing with all trades.

- Review any Engineering Judgments or other special requirements.

- Function and frequency of inspections and testing labs.

  - Coordinate areas prior to firestopping installation with the Owner, Construction Manager and/or all other Contractors.

  - Coordinate construction of openings and penetrating items to ensure that firestopping assemblies and fire-resistant joint systems are installed according to their respective system’s listing. Openings shall not exceed maximum sizes allowable for annular spacing per listing or acceptable Engineering Judgments.

  - Coordinate sizing of sleeves, openings, core-drilled holes, or cut openings to accommodate through-penetration firestop systems.

  - Schedule firestopping after installation of penetrants and joints but prior to concealing or obstructing access to areas requiring firestopping.

  - Do not conceal firestopping installations until the Owner’s inspection agency and Authorities Having Jurisdiction have examined each installation.

  - The Owner may elect to perform destructive testing at mockup and at predetermined or random intervals according to ASTM E2174 and ASTM E2393 by the inspector and with the installing Contractor present. Inspector to test for in place installation conformance to tested and listed system or Engineering Judgment details. Non conformances will result in additional destructive testing, at the cost of the installer. Repairs to be provided by contractor until it has been determined that systems have been completed in accordance with their respective listing.

## PART 2 - PRODUCTS

- FIRESTOPPING, GENERAL

  - Firestopping products specified in system design listings by approved testing agencies may be used provided they conform to the construction type, penetrant type, annular space requirements and fire rating involved in each separate assembly.

  - Accessories: Provide components for each firestop system that are needed to install fill materials and to comply with “Performance Requirements” Article. Use only components specified by the firestopping manufacturer and by the approved testing agencies for the firestop systems indicated. Accessories include, but are not limited to the following items:

    - Permanent forming/damming/backing materials, including the following:

      - Rock or slag wool fiber insulation.

      - Foams or sealants used to prevent leakage of fill materials in liquid state.

      - Fire-rated form board.

      - Polyethylene/polyurethane backer rod.

      - Rigid polystyrene board.

    - Temporary forming materials.

    - Substrate primers.

    - Steel sleeves.

  - All firestopping products and systems shall be designed and installed so that the basic sealing system will allow the full restoration of the thermal and fire resistance properties of the rated assembly being penetrated with minimal repair if penetrants are subsequently removed.

- MIXING

  - For those products requiring mixing before application, comply with firestopping manufacturer’s written instructions for accurate proportioning of materials, water (if required), type of mixing equipment, selection of mixer speeds, mixing containers, mixing time, and other items or procedures needed to produce products of uniform quality with optimum performance characteristics for application indicated.

- MANUFACTURERS

  - Subject to compliance with the requirements, provide products by one of the following or equivalent manufacturers:

    - Grace Construction Products.

    - Nelson Firestop Products.

    - Hilti Firestop Products.

    - A/D Fire Protection Systems Inc.

    - RectorSeal Corporation (The).

    - Specified Technologies Inc.

    - 3M; Fire Protection Products Division.

    - Tremco; Sealant/Weatherproofing Division.

## PART 3 - EXECUTION

- EXAMINATION

  - Examine substrates and conditions for compliance with requirements for opening configurations, penetrating items, substrates, and other conditions affecting performance.

  - Proceed with installation only after unsatisfactory conditions have been corrected.

  - Verify that all pipes, conduits, cables, and/or other items which penetrate fire-rated construction have been permanently installed prior to installation of firestops.

- PREPARATION

  - Surface Cleaning:  Clean out openings immediately before installing firestop systems to comply with written recommendations of firestopping manufacturer and the following requirements:

    - Remove from surfaces of opening substrates and from penetrating items foreign materials that could interfere with adhesion of firestop systems.

    - Clean opening substrates and penetrating items to produce clean, sound surfaces capable of developing optimum bond with firestop systems. Remove loose particles remaining from cleaning operation.

    - Remove laitance and form-release agents from concrete.

  - Verify that the field conditions are representative of and match the firestop systems that have been selected. Where deviations occur and listed firestop systems are unable to be identified, refer to Section 1.5, D for Engineering Judgment.

  - For cast-in place firestop devices, coordinate device locations with all other trades.

- FIRESTOP AND FIRE-RESISTANT JOINT SYSTEMS INSTALLATION

A.	General: Install firestop systems and fire-resistant joint systems to comply with “Performance Requirements” article in Part 1 and firestopping manufacturer’s written installation instructions and published drawings for products and applications indicated.

  - Installation of firestopping and fire-resistant joint systems shall be performed by an applicator/installer qualified as described in article 1.7.

  - Apply firestopping and fire-resistant joint systems in accordance with approved testing agencies listed system designs or manufacturer’s EJ per the manufacturer’s installation instructions.

  - Verify that environmental conditions are suitable for installation of firestop products.

  - Install forming/damming/backing materials and other accessories required to support fill materials during their application and in the position needed to produce cross-sectional shapes and depths to achieve fire resistance ratings required.

    - After installing fill materials and allowing them to fully cure, remove combustible forming materials and other accessories not forming permanent components of firestopping.

  - Install joint forming/damming materials and other accessories required to support fill materials during their application and in the position needed to produce cross-sectional shapes and depths of installed firestopping material relative to joint widths that allow optimum movement capability and achieve fire resistance ratings required.

  - Install metal framing, curtain wall insulation, mechanical attachments, safing materials and firestop materials as applicable within the system design.

  - Install fill materials for firestopping and fire-resistant joint systems by proven techniques to produce the following results:

    - Fill voids, joints and cavities formed by openings, forming materials, accessories, and penetrating items as required to achieve fire-resistance ratings indicated.

    - Apply materials so they fully contact and adhere to substrates formed by openings and penetrating items.

    - Fill materials shall be located within the annular space created between a penetrating material and the adjacent construction for the full depth specified, unless detailed by the listing of the firestop system or Engineering Judgment for point of contact application or as otherwise described.

    - For fill materials that will remain exposed after completing Work, finish to produce smooth, uniform surfaces that are flush with adjoining finishes.

    - Tool non-sag firestop materials after their application and prior to the time skinning begins. Use tooling agents approved by the firestopping manufacturer.

  - On vertical pipe penetrations protected from the top side of a floor, lift riser clamps to permit the installation of firestop systems around the entire pipe penetration and within the annular space created between the penetrating material and the adjacent construction.

  - On insulated material penetrations such as would accompany pipes, ensure the insulation is installed continuous through the opening and the insulation material is consistent with the type described by the firestop system’s listing.

  - Where penetrating materials are not continuous on one or both sides of a fire-resistance rated assembly, such as would occur with EMT sleeves filled with cables, ensure the listed firestop system details such, fully describes protection of the open ends, and is installed in accordance with the system’s listing.

  - For penetrations involving fire or fire/smoke dampers, only firestop products approved by the damper manufacturer shall be installed in accordance with the damper installation instructions.

  - Finishes over firestop systems such as paint or joint compound, or covering firestops with materials such as gypsum wallboard, shall be permitted only where it is explicitly stated as such by the manufacturer or their system installation instructions.

  - Install firestop devices in accordance with the manufacturer’s written instructions and the firestop system’s listing. Use fasteners as specified by the firestop system and in sufficient quantity as described. Where wrap strips, plugs, or other additional firestop components are required after pulling or routing materials, install them as specified by the firestop system listing.

  - Following firestop installation, promptly install labels as described in Section 1.7, G.

- IDENTIFICATION

  - Wall Identification: Where there is an accessible concealed floor, floor-ceiling or attic space, fire walls, fire barriers, fire partitions, smoke barriers and smoke partitions or any other wall required to have protected openings or penetrations shall be effectively and permanently identified with signs or stenciling in the concealed space. Such identification shall:

    - Be located within 15 feet (4572 mm) of the end of each wall and at intervals not exceeding 30 feet (9144 mm) measured horizontally along the wall or partition.

    - Include lettering not less than 3 inches (76 mm) in height with a minimum 3/8-inch (9.5 mm) stroke in a contrasting color incorporating the suggested wording, "FIRE AND/OR SMOKE BARRIER-PROTECT ALL OPENINGS," or other wording.

  - Do not install adhered or painted markings when ambient temperature is lower than recommended by label, sign, or coating manufacturer.

  - Signs and stenciling shall be protected from damage until Date of Substantial Completion. Repair or replace damaged wall identification.

- FIELD QUALITY CONTROL

  - Inspecting Agency: Authorities Having Jurisdiction, the Owner, or Owner’s Representative shall be allowed to perform random destructive testing during inspection of firestop systems to verify compliance per listings or manufacturer’s installation instructions. All areas of work must be accessible until inspection by the applicable Authorities Having Jurisdiction and inspection agencies. The contractor shall be responsible to repair all tested assemblies with no cost to the owner.

  - Proceed with enclosing firestop systems with other construction only after inspections are complete.

  - Where deficiencies are found, repair or replace firestop systems so they comply with requirements.

  - Where special inspections are required to be performed for penetration firestops in accordance with the requirements of ASTM E2174, the final report defined by Part 12 of that standard shall be provided to the Owner.

  - Where special inspections are required to be performed for fire-resistant joint systems in accordance with the requirements of ASTM E2393, the final report defined by Part 12 of that standard shall be provided to the Owner.

- CLEANING AND PROTECTION

  - Clean off excess fill materials adjacent to openings as Work progresses by methods and with cleaning materials that are approved in writing by firestopping manufacturer(s) and that do not damage materials in which openings occur. Leave finished work in neat, clean condition with no evidence of spillovers or damage to adjacent surfaces.

  - Provide final protection and maintain conditions during and after installation that ensure firestop systems are without damage or deterioration at time of Substantial Completion. If, despite such protection, damage or deterioration occurs, cut out and remove damaged or deteriorated firestop systems immediately and install new materials to produce firestop systems complying with specified requirements.

EXAMPLE FIRESTOP SCHEDULE

| Project No: 1234569999 | Contractor Name and Address: Example General Contractor 515 Broadway Albany, NY 12207 | Date Submitted: 1/23/2025 |
| --- | --- | --- |
| Project Title: Example Project Facility Broadway, Albany, NY 12207 Building Number Project Type | Supplier/Installer Name and Address: Example Firestop Installer 515 Broadway, Albany, NY 12207 | Company Field Advisor Name and Address: Firestop Supervisor Firestop Ln, Firestopville, NY 12345 |
|  | Manufacturer Name and Address: Examples: Hilti, Inc, or 3M, or STI Firestop Ln, Firestopville, NY, 12345 |  |

| Manufacturer's Product Reference Numbers and/or Drawing Numbers | U.L., FM, Warnock Hersey, Intertek or other Testing Lab Penetration Design Numbers | Penetrating Item: Material, Size, Insulated, Combustible, Joint, Perimeter, etc. Description: | Maximum Allowable Annular Space or Maximum Size Opening | Wall or floor type Construction |  | Fire Resistance Rating of Wall or Floor (Hourly) | F Rating | T Rating (floors Only) | L Rating (if available) | W Rating (if available) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | DES. | CONST. |  |  |  |  |  |
| Example No. 1 Hilti | C-AJ-1155 | Max 6" Copper Pipe, 4" 4pcf mineral wool, 1/2" FS-One Max | 0-12" for 2-Hour 0-2.25" for 3-Hour | Conc-rete | 4.5” | 2-hr or 3-hr | 2 or 3-Hour |  | 4 cfm/ft | Class 1 |
| Example No. 2 Hilti | EJ: 664498a | Max 3/4" Nominal Copper Pipe, Max 1" Thick EPDM Insulation, Min 5/8" FS-One Max or 1/2" at point of contact | 0-1.25" annular space, Max 4" opening | Block | 8” CMU | 2-Hour Rating | 2-Hour |  |  |  |
| Example No. 3 3M | CW-S-2006 | Bottom of wall joint, gypsum stud wall, concrete slab, 5/8" depth CP 25WB+ | 1” | UL U419 | Metal stud, gyp. board | 1-hr wall / 1-hr floor | 1-Hour |  | <1 cfm / ft^2 |  |
| Example No. 4 3M | C-AJ-2377 | Max. 3" Sched. 40 PVC/SDR13.5 pipe 3" 4pcf mineral wool, 1/2" CP 25WB+ | Max 5" diam. opening Min. 1/2"/Max 1" annular space | Conc-rete, CMU, precast | 4.5” wall, 6” precast | 2-Hour Rating | 2-Hour | 2-Hour | <1 cfm / ft^2 | Class 1 |
| Example No. 5 STI | C-AJ-2373 | Max. 4" Sched. 40 PVC/SDR13.5 pipe 2 layers wrap strip, 1/4" Metacaulk 1000 | Max 6" diam. Opening 1/2" annular space | Conc-rete, CMU, precast | 4.5” wall, 8” precast, 6” CMU | 1/2- and 2-Hour Rating | 1/2 or 2- Hour | 2-Hour |  |  |
| Example No. 6 STI | CW-D-1004 | Curtain wall joint, concrete slab, curtain wall assembly, spandrel system, mineral wool, safing system | Max 4" edge separation, Min 1/16" dry thickness spray, 1/2" lap | Conc-rete, curtain wall | 4.5” slab | 2-Hour | 2-Hour | 1/2-Hour | <1 cfm/ft |  |

FIRESTOP SCHEDULE

| Project No: | Contractor Name and Address: | Date Submitted: |
| --- | --- | --- |
| Project Title: | Supplier/Installer Name and Address: | Company Field Advisor Name and Address: |
|  | Manufacturer Name and Address: |  |

| Manufacturer's Product Reference Numbers and/or Drawing Numbers | U.L., FM, Warnock Hersey, Intertek or other Testing Lab Penetration Design Numbers | Penetrating Item: Material, Size, Insulated, Combustible, Joint, Perimeter, etc. Description: | Maximum Allowable Annular Space or Maximum Size Opening | Wall or floor type Construction |  | Fire Resistance Rating of Wall or Floor (Hourly) | F Rating | T Rating (floors Only) | L Rating (if available) | W Rating (if available) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | DES. | CONST. |  |  |  |  |  |