FIRESTOPPING SPECIFICATION

SECTION 078400 - FIRESTOPPING

## PART 1 – GENERAL

- RELATED DOCUMENTS

  - Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

- SUMMARY

  - Provide firestop systems consisting of a material, or combination of materials installed to retain the integrity of fire resistance rated construction by maintaining an effective barrier against the spread of flame, smoke and/or hot gases through penetrations, fire resistive joints, and perimeter openings in accordance with the requirements of the Building Code for this project.

  - Firestop systems shall be used in locations including, but not limited to, the following:

    - Penetrations through fire resistance rated floor and roof assemblies including both empty openings and openings containing penetrants.

    - Penetrations through fire resistance rated wall assemblies including both empty openings and openings containing penetrants.

    - Membrane penetrations in fire resistance rated wall assemblies where items penetrate one side of the barrier.

    - Joints between fire resistance rated assemblies.

    - Perimeter gaps between rated floors/roofs and an exterior wall assembly.

  - Related Sections include, but are not limited to, the following:

    - Division 07 – Thermal and Moisture Protection

    - Division 09 – Finishes

    - Division 21 – Fire Suppression

    - Division 22 – Plumbing

    - Division 23 – Heating, Ventilating and Air Conditioning

    - Division 25 - Automation

    - Division 26 – Electrical

    - Division 27 – Communications

    - Division 28 – Electrical Safety and Security

- REFERENCES

  - New York State Uniform Fire Prevention and Building Code  (New York City Building Code) Editing Note: change according to location and code authority for project.

  - National Fire Protection Association (NFPA)

    - NFPA 101 (Life Safety Code)

  - American Society For Testing and Materials Standards (ASTM):

    - ASTM E84:	Standard Test Method for Surface Burning Characteristics of Building Materials.

    - ASTM E814:	Standard Test Method for Fire Tests of Through-Penetration Firestops.

    - ASTM E1966:	Test Method for Resistance of Building Joint Systems.

    - ASTM E1399:	Test Method for Cyclic Movement and Measuring Minimum and Maximum Joint Width.

    - ASTM E119:	Methods of Fire Tests of Building Construction and Materials.

    - ASTM E2174:	Standard Practice for On-Site Inspection of Installed Fire Stops

    - ASTM E2307:	Standard Test Method for Determining the Fire Endurance of Perimeter Fire Barrier Systems Using the Intermediate-Scale, Multi Story Test Apparatus (ISMA)

    - ASTM E2393-04 Standard Practice for On-Site Inspection of Installed Fire Resistive Joint Systems and Perimeter Fire Barriers

  - Underwriters Laboratories Inc. (UL):

    - UL Qualified Firestop Contractor Program.

    - UL 263:	Fire Tests of Building Construction and Materials.

    - UL 723:	Surface Burning Characteristics of Building Materials.

    - UL 1479:	Fire Tests of Through-Penetration Fire Stops.

    - UL 2079:	Tests for Fire Resistance of Building Joint Systems.

  - UL Fire Resistance Directory -Volume 2:

    - Through-Penetration Firestop Devices (XHJI)

    - Fire Resistive Ratings (BXUV)

    - Through-Penetration Firestop Systems (XHEZ)

    - Fill, Void, or Cavity Material (XHHW)

  - Omega Point Laboratories (OPL)

    - Building Products, Materials & Assemblies – Volume II

  - Factory Mutual Research (FM):

    - FM 4991:	FM Approval Standard of Firestop Contractors – Class 4991

- DEFINITIONS

  - Firestopping:  The use of a material or combination of materials in a fire-rated structure (wall or floor) where it has been breached, so as to restore the integrity of the fire rating on that wall or floor.

  - System:  The use of a specific firestop material or combination of materials in conjunction with a specific wall or floor construction type and a specific penetrant(s).

  - Barrier:  Any bearing or non-bearing wall or floor that has an hourly fire and smoke rating.

  - Through-penetration:  Any penetration of a fire-rated wall or floor that completely breaches the barrier.

  - Membrane-penetration:  Any penetration in a fire-rated wall or floor/roof-ceiling assembly that breaches only one side of the barrier.

  - Fire Resistive/Construction Joint:  Any gap, joint, or opening, whether static or dynamic, between two fire rated barriers including where the top of a wall meets a floor; wall edge to wall edge applications; floor edge to floor edge configurations; floor edge to wall.

  - Perimeter Barrier: Any gap, joint, or opening, whether static or dynamic, between a fire rated floor assembly and an exterior wall assembly.

  - Approved Testing Agencies: Not limited to: Underwriters Laboratory (UL), Factory Mutual (FM), Warnock Hersey, and Omega Point Laboratory (OPL).

- PERFORMANCE REQUIREMENTS

  - Penetrations: Provide through-penetration and membrane-penetration firestop systems that are produced and installed to resist the spread of fire, passage of smoke and other hot gases according to requirements indicated, to restore the original fire-resistance rating of assembly penetrated.

    - Provide and install complete penetration firestopping systems that have been tested and approved by nationally accepted testing agencies per ASTM E814 or UL 1479 fire tests in a configuration that is representative of field conditions.

    - F-Rated Systems:  Provide firestop systems with F-ratings indicated, as determined per ASTM E814 or UL 1479, but not less than one (1) hour or the fire resistance rating of the assembly being penetrated.

    - T-Rated Systems: Provide firestop systems with T-ratings indicated, as well as F-ratings, as determined per ASTM E814 or UL 1479, where required by the Building Code.

    - L- Rated Systems: Provide firestop systems with L- ratings less than 5cfm/sf.

    - W-Rated systems: Provide firestop systems that are resistant to water.  For piping penetrations for plumbing and wet-pipe sprinkler systems, provide moisture-resistant through-penetration firestop systems.

    - For penetrations involving non-metallic, CPVC, PVC, or plastic piping, tubing or conduit, provide firestop systems that are chemically compatible in accordance with Manufacturer requirements.

    - For penetrations involving insulated piping, provide firestop systems not requiring removal of insulation.

    - For penetrations involving fire or fire/smoke dampers, only firestop products approved by the damper manufacturer shall be installed in accordance with the damper installation instructions.

  - Fire Resistive Joints: Provide joint systems with fire resistance assembly ratings indicated, as determined by UL 2079 (ASTM E1399 and E1966), but not less than the fire resistance assembly rating of the construction in which the joint occurs.  Firestopping assemblies must be capable of withstanding anticipated movements for the installed field conditions.

    - For firestopping assemblies exposed to view, traffic, moisture, and physical damage, provide products that after curing do not deteriorate when exposed to these conditions both during and after construction.

    - For floor penetrations exposed to possible loading and traffic, provide firestop systems capable of supporting floor loads involved either by installing floor plates or by other means, as specified by the Architect.

    - L- Rated Systems: Provide firestop systems with L- ratings less than 5cfm/sf.

  - Firestopping products shall have flame spread ratings less than 25 and smoke-developed ratings less than 450, as determined per ASTM E 84.  Note: Firestop products installed in plenum spaces shall have a smoke developed rating less that 50.

  - Engineering Judgment (EJ): Where there is no specific third party tested and classified firestop system available for an installed condition, the Contractor shall obtain from the firestopping material manufacturer an Engineering Judgment (EJ) to be submitted to the Approving Authority, Design Professional and Authority Having Jurisdiction for approval prior to installation.  The EJ shall follow International Firestop Council (IFC) guidelines.

- SUBMITTALS

  - Product Data:  For each type of firestopping product selected.  Manufacturers certification must verify that firestopping materials are free of asbestos, lead and contain volatile organic compounds (VOCs) within limits of the local jurisdiction.

  - Design Listings:  Submit system design listings, including illustrations, from a qualified testing and inspecting agency that is applicable to each firestop configuration.

  - Installation Instructions: Submit the manufacturer’s installation instruction for each firestop assembly.

  - Where there is no specific third party tested and classified firestop system available for a particular configuration, the Contractor shall obtain from the firestopping material manufacturer an Engineering Judgment (EJ) for submittal.

  - Material Safety Data Sheet (MSDS): Submit for each type of firestopping product selected.

  - Qualification Data: For firms and persons specified in “Quality Assurance” Article to demonstrate their capabilities and experience.  Submit documents as per 1.7.

  - A quality control manual approved by FM or UL (if applicable).

  - Firestop Schedule:  Submit schedule (see appendix A)  itemizing the following:

    - Manufacturer’s product reference numbers and/or drawing numbers.

    - Listing agency’s design number.

    - Penetrating Item Description/Limits:  Material, size, insulated or uninsulated, and combustibility.

    - Maximum allowable annular space or maximum size opening.

    - Wall type construction.

    - Floor type construction.

    - Hourly Fire resistance rating of wall or floor.

    - F rating.

    - T, L, and W rating, if applicable.

  - Firestop Application Log: A separate binder shall be prepared and kept on site for use by the Inspection Agency and the Authority Having Jurisdiction.  The binder shall contain the following:

    - The binder shall be a three (3) ring binder.

    - Firestop Schedule (see appendix A)

    - All approved firestopping assemblies including engineering judgments shall be provided and organized by trade.

    - Copy of manufacturer’s installation instruction for each firestop assembly.

    - A matrix or table of contents listing each assembly shall be provided.

    - The binder shall be updated as new firestop assemblies or EJ’s are added.

    - The binder shall be kept on-site at a location approved by the Owner.

    - Qualifications or Certification of Installer

- QUALITY ASSURANCE

  - Provide firestopping system design listings from UL, FM, Warnock Hersey or OPL in accordance with the appropriate ASTM Standard(s) per article 1.5.

  - Contractor Qualifications:  An acceptable Firestop Contractor shall  be:

    - Licensed by State or Local Authority where applicable, or

    - FM Research approved in accordance with FM Standard 4991, or

    - UL Qualified Firestop Contractor, or

    - Meet the following requirements

      - Installation personnel shall be trained by the approved firestop manufacturer.

      - The installation firm shall be experienced in installing firestop systems and fire resistive joint systems similar in material, design, and extent to that indicated for this Project, whose work has resulted in construction with a record of successful performance.

      - Qualifications include having the necessary experience, staff, and training to install manufacturer's products per specified tested and listed system requirements.

      - Minimum of three (3) years experience and shown to have successfully completed not less than 5 comparable scale projects and provide references.

  - Single Source Limitations:  Obtain firestop systems for all conditions from a single manufacturer.

  - Materials from different firestop manufacturers shall not be installed in the same firestop system or opening.

  - Firestopping material shall be asbestos and lead free and shall not incorporate nor require the use of hazardous solvents.

  - Firestopping sealants must be flexible, allowing for normal movement.

  - Firestopping materials shall not shrink upon drying as evidenced by cracking or pulling back from contact surfaces such that a void is created.

  - Firestopping materials shall be moisture resistant, and may not dissolve in water after curing.

  - Materials used shall be in accordance with the manufacturer’s written installation instructions.

  - Identify installed firestop systems with preprinted metal or plastic labels.  Attach labels permanently to surfaces adjacent to and within 6 inches (150 mm) of edge of the firestop systems so that labels will be visible to anyone seeking to remove penetrating items or firestop systems.  Use mechanical fasteners for metal labels.  For plastic labels, use self-adhering type with adhesives capable of permanently bonding labels to surfaces on which labels are placed and provide a label material that will result in partial destruction of label if removal is attempted.  Include the following information on labels:

    - The words "Warning - Firestop System - Do Not Disturb.  Notify Building Management of Any Damage."

    - Contractor's name, address, and phone number.

    - Firestop system designation of applicable testing and listing agency.

    - Date of installation.

    - Firestop system manufacturer's name.

    - Installer's name.

    - Inspector’s name (if applicable)

  - Inspection of penetrations through fire rated floor and wall assemblies shall be in accordance with 
ASTM E2174, Standard Practice for On-Site Inspection of Installed Fire Stops and ASTM E2393-04 Standard Practice for On-Site Inspection of Installed Fire Resistive Joint Systems and Perimeter Fire Barriers.  The Owner may engage a qualified, independent inspection agency, or material testing agency to perform these inspections.  (Editing Note: NYC Projects are subject to the requirements of Special Inspections in accordance with Chapter 17 of the 2008 NYC Building Code.)

  - Field Mock-up Installations:  Prior to installing firestopping, erect mock-up installations for each type firestop system indicated in the Firestop Schedule to verify selections made and to establish standard of quality and performance by which the firestopping work will be judged by the Owner or Owner’s Representative.  Obtain acceptance of mock-up installations by the Owner or Owner’s Representative before start of firestopping installation.  Provide at least 72 hours notice to Owner or Owner’s Representative prior to inspection.

- DELIVERY, STORAGE, AND HANDLING

  - Deliver firestopping products to Project site in original, unopened containers or packages with intact and legible manufacturer’s labels identifying product and manufacturer, date of manufacture/expiration, lot number, listing agency’s classification marking, and mixing instructions for multi-component materials.

  - Store and handle materials per manufacturer’s instructions to prevent deterioration or damage due to moisture, temperature changes, contaminants, or other causes.

  - All firestop materials shall be installed prior to expiration date.

- PROJECT CONDITIONS

  - Environmental Limitations:  Install firestopping when ambient or substrate temperatures are within limits permitted by the manufacturer’s written instructions.  Do not install firestopping when substrates are wet due to rain, frost, condensation, or other causes.

  - Ventilate per the manufacturers written instructions on the product’s Material Safety Data Sheet.

  - Verify the condition of the substrates before starting work.

  - Care should be taken to ensure that firestopping materials are installed so as not to contaminate adjacent surfaces.

- COORDINATION

  - Coordinate areas prior to firestopping installation with the Owner, Construction Manager and/or all other Contractors.

  - Coordinate construction of openings and penetrating items to ensure that firestopping assemblies are installed according to specified requirements.  Opening shall not exceed maximum restrictions allowable for annular spacing per listing or acceptable Engineering Judgments.

  - Coordinate sizing of sleeves, openings, core-drilled holes, or cut openings to accommodate through-penetration firestop systems.

  - Do not conceal firestopping installations until the Owner’s inspection agency or Authorities Having Jurisdiction have examined each installation.

  - Schedule firestopping after installation of penetrants and joints but prior to concealing or obstructing access to areas requiring firestopping.

  - Preinstallation Conference:  This conference should be a joint meeting attended by the Owner’s Representative and all prime contractors, respective firestopping sub-contractors and firestopping company field advisor to review project requirements.  The agenda for the conference should include the following topics:

- Review scope of work.

- Review shop drawings and firestop application log.

- Review mock-up requirements.

- Discuss identification labels and locations.

- Review schedule, coordination and sequencing with all trades.

- Review any engineering judgments or other special requirements.

- Function and frequency of inspections and testing labs.

  - Destructive testing shall be performed at mock up and at pre determined intervals according to ASTM E 2174 and ASTM E 2393-04 by the inspector and with the installing Contractor  present.  Inspector to test for in place installation conformance to tested and listed system or engineering judgment details.  Non conformances will result in additional destructive testing, at the cost of the installer.

## PART 2 - PRODUCTS

- FIRESTOPPING, GENERAL

  - Firestopping products specified in system design listings by approved testing agencies may be used providing they conform to the construction type, penetrant type, annular space requirements and fire rating involved in each separate assembly.

  - Manufacturer of firestopping products shall have been successfully producing and supplying these products for a period of not less than three years and be able to show evidence of at least ten projects where similar products have been installed and accepted.

  - Accessories:  Provide components for each firestop system that is needed to install fill materials and to comply with “Performance Requirements” Article.  Use only components specified by the firestopping manufacturer and by the approved testing agencies for the firestop systems indicated.  Accessories include, but are not limited to the following items:

    - Permanent forming/damming/backing materials, including the following:

      - Slag wool fiber insulation.

      - Foams or sealants used to prevent leakage of fill materials in liquid state.

      - Fire-rated form board.

      - Polyethylene/polyurethane backer rod.

      - Rigid polystyrene board.

    - Temporary forming materials.

    - Substrate primers.

    - Steel sleeves

  - All firestopping products and systems shall be designed and installed so that the basic sealing system will allow the full restoration of the thermal and fire resistance properties of the barrier being penetrated with minimal repair if penetrants are subsequently removed.

- MIXING

  - For those products requiring mixing before application, comply with firestopping manufacturer’s written instructions for accurate proportioning of materials, water (if required), type of mixing equipment, selection of mixer speeds, mixing containers, mixing time, and other items or procedures needed to produce products of uniform quality with optimum performance characteristics for application indicated.

- MANUFACTURERS

  - Subject to compliance with the requirements, provide products by one of the following or equivalent manufacturers:

    - Grace Construction Products.

    - Nelson Firestop Products.

    - Hilti Firestop Products.

    - A/D Fire Protection Systems Inc.

    - RectorSeal Corporation (The).

    - Specified Technologies Inc.

    - 3M; Fire Protection Products Division.

    - Tremco; Sealant/Weatherproofing Division.

## PART 3 - EXECUTION

- EXAMINATION

  - Examine substrates and conditions for compliance with requirements for opening configurations, penetrating items, substrates, and other conditions affecting performance.

  - Proceed with installation only after unsatisfactory conditions have been corrected.

  - Verify that all pipes, conduits, cables, and/or other items which penetrate fire-rated construction have been permanently installed prior to installation of firestops.

- PREPARATION

  - Surface Cleaning:  Clean out openings immediately before installing firestop systems to comply with written recommendations of firestopping manufacturer and the following requirements:

    - Remove from surfaces of opening substrates and from penetrating items foreign materials that could interfere with adhesion of firestop systems.

    - Clean opening substrates and penetrating items to produce clean, sound surfaces capable of developing optimum bond with firestop systems.  Remove loose particles remaining from cleaning operation.

    - Remove laitance and form-release agents from concrete.

3.3	FIRESTOP SYSTEMS INSTALLATION

A.	General:  Install firestop systems to comply with “Performance Requirements” article in Part 1 and firestopping manufacturer’s written installation instructions and published drawings for products and applications indicated.

  - Installation of firestopping shall be performed by an applicator/installer qualified as described in article 1.7.

  - Apply firestopping in accordance with approved testing agencies listed system designs or manufacturer’s EJ per the manufacturer’s installation instructions.

  - Verify that environmental conditions are safe and suitable for installation of firestop products.

  - Install forming/damming/backing materials and other accessories required to support fill materials during their application and in the position needed to produce cross-sectional shapes and depths required to achieve fire resistance ratings required.

  - Install joint forming/damming materials and other accessories required to support fill materials during their application and in the position needed to produce cross-sectional shapes and depths of installed firestopping material relative to joint widths that allow optimum movement capability and achieve fire resistance ratings required.

  - Install metal framing, curtain wall insulation, mechanical attachments, safing materials and firestop materials as applicable within the system design.

  - Install fill materials for firestop systems by proven techniques to produce the following results:

    - Fill voids, joints and cavities formed by openings, forming materials, accessories, and penetrating items as required to achieve fire-resistance ratings indicated.

    - Apply materials so they fully contact and adhere to substrates formed by openings and penetrating items.

    - For fill materials that will remain exposed after completing Work, finish to produce smooth, uniform surfaces that are flush with adjoining finishes.

    - Tool non-sag firestop materials after their application and prior to the time skinning begins.  Use tooling agents approved by the firestopping manufacturer.

  - On vertical pipe penetrations, lift riser clamps to permit the installation of firestopping around the entire pipe penetration.  For penetrations involving fire or fire/smoke dampers, only firestop products approved by the damper manufacturer shall be installed in accordance with the damper installation instructions.

3.4	FIELD QUALITY CONTROL

  - Inspecting Agency:  Authorities Having  Jurisdiction, the Owner, or Owner’s Representative shall be allowed to perform random destructive testing during inspection of firestop systems to verify compliance per listings or manufacturer’s installation instructions.  All areas of work must be accessible until inspection by the applicable Authorities Having Jurisdiction and inspection agencies.  The contractor shall be responsible to repair all tested assemblies with no cost to the owner.

  - Proceed with enclosing firestop systems with other construction only after inspections are complete.

  - Where deficiencies are found, repair or replace firestop systems so they comply with requirements.

  - CLEANING AND PROTECTION

  - Clean off excess fill materials adjacent to openings, as Work progresses by methods and with cleaning materials that are approved in writing by firestopping manufacturer(s) and that do not damage materials in which openings occur.  Leave finished work in neat, clean condition with no evidence of spillovers or damage to adjacent surfaces.

  - Provide final protection and maintain conditions during and after installation that ensure firestop systems are without damage or deterioration at time of Substantial Completion.  If, despite such protection, damage or deterioration occurs, cut out and remove damaged or deteriorated firestop systems immediately and install new materials to produce firestop systems complying with specified requirements.

FIRESTOP SCHEDULE

| Project No: | Contractor Name and Address: | Date Submitted: |
| --- | --- | --- |
| Project Title: | Supplier/Installer Name and Address: | Company Field Advisor Name and Address: |
|  | Manufacturer Name and Address: |  |

| Manufacturer's Product Reference Numbers and/or Drawing Numbers | U.L., FM, Warnock Hersey or Omega Point Lab Penetration Design Nos. | Penetrating Item: Material, Size, Insulated, Combustible, Joint, Perimeter, etc. Description: | Maximum Allowable Annular Space or Maximum Size Opening | Wall type Construction |  | Floor Type Construction | Fire Resistance Rating of Wall or Floor (Hourly) | F Rating | T Rating (floors Only) | L Rating (if available) | W Rating (if available) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | DES. | CONST. |  |  |  |  |  |  |
| Example No. 1 DCFSS-130 | UL #130 | Maximum 4" Steel Pipe Non-Insulated |  | P4 | 6" CMU | N.A. | 1 Hour | 1 Hour | N.A | . |  |
| Example No. 2 5300-ICF88.01 | UL #591 | Maximum 4" PVC Pipe |  | N.A. | N.A. | UL # D916 | 3 Hour | 1 Hour | 2 Hour |  |  |
| Exmple No. 3 | CW-S-2006 | Curtain Wall/Perimeter | 6” to 12” | NA | NA | 4 ½” Reinforced LW concrete | 2 Hour | 2 Hour | NA | 1 CFM/ Lin Ft. |  |