|  | 2020 NYS BUILDING CODE STATEMENT OF SPECIAL INSPECTIONS. |
| --- | --- |
| BCNYS §1704.3 requires that the project Registered Design Professional in responsible charge prepare a Statement of Special Inspections. Completion of this Statement of Special Inspections and submission to the Code Compliance Unit with the Construction Permit Application is a condition for issuance of the Construction Permit. |  |  |  |  |
| Campus/Facility: |  |  |  |  |
| Project Title: |  |  |  |  |
| Project #: |  | DASNY Project Manager: |  |  |
| Registered Design Professional (RDP): |  |  |  |  |
| Name of Person Completing Statement: |  |  | Phone: | Date: |
| Comments: |  |  |  |  |

| INSPECTIONS AND TESTS (Continuous & Periodic is as defined by the BCNYS) | CONTINUOUS | PERIODIC | BCNYS REFERENCE | CHECK IF REQUIRED | SPECIFICATION REFERENCE AND CLARIFYING NOTES (by RDP)1 | COMMENTARY/NOTES and REFERENCE STANDARDS (by DASNY)2 |
| --- | --- | --- | --- | --- | --- | --- |
| ## A. Special Cases (Add requirements under Part S as necessary) |  |  | 1705.1.1 |  |  | Special Inspections and Tests shall be required for proposed work that is, in the opinion of the building official, unusual in its nature. |
| ## B. Steel Construction. |  |  | 1705.2 |  |  |  |
| - Structural Steel |  |  | ## 1705.2.1 |  |  |  |
| a. Inspection tasks prior to welding; |  |  | ## 1705.2.1 |  |  | ## AISC 360 Table N5.4-1 |
| i. Welding procedure specifications (WPSs) available | ## X |  | ## 1705.2.1 |  |  | ## AISC 360 Table N5.4-1 |
| ii. Manufacturer certifications for welding consumables available | ## X |  | ## 1705.2.1 |  |  | ## AISC 360 Table N5.4-1 |
| iii. Material identification (type/grade) |  | ## X | ## 1705.2.1 |  |  | ## AISC 360 Table N5.4-1 |
| iv. Welder identification system |  | ## X | ## 1705.2.1 |  |  | ## AISC 360 Table N5.4-1 ## The fabricator or erector, as applicable, shall maintain a system by which a welder who has welded a joint or member ## can be identified. Stamps, if used, shall be the low-stress ## type. |
| v. Fit up of groove welds (including joint geometry) |  | ## X | ## 1705.2.1 |  |  | ## AISC 360 Table N5.4-1 |
| vi. Configuration and finish of access holes |  | ## X | ## 1705.2.1 |  |  | ## AISC 360 Table N5.4-1 |
| vii. Fit-up of fillet welds |  | ## X | ## 1705.2.1 |  |  | ## AISC 360 Table N5.4-1 |
| viii. Check Welding equipment |  | ## X | ## 1705.2.1 |  |  | ## AISC 360 Table N5.4-1 |
| b. Inspection Tasks During Welding |  |  | ## 1705.2.1 |  |  | ## AISC 360 Table N5.4-2 |
| i. Use of qualified welders. |  | ## X | 1705.2.1 |  |  | AISC 360 Table N5.4-2 |
| ii. Control and Handling of welding consumables. |  | ## X | 1705.2.1 |  |  | AISC 360 Table N5.4-2 |
| iii. No welding over cracked tack welds. |  | ## X | 1705.2.1 |  |  | AISC 360 Table N5.4-2 |
| iv. Environmental Conditions |  | ## X | 1705.2.1 |  |  | AISC 360 Table N5.4-2 |
| v. Verify WPS followed |  | ## X | 1705.2.1 |  |  | AISC 360 Table N5.4-2 |
| vi. Verify Welding Techniques |  | ## X | 1705.2.1 |  |  | AISC 360 Table N5.4-2 |
| c. Inspection Tasks after Welding |  |  | 1705.2.1 |  |  | AISC 360 Table N5.4-3 |
| i. Welds cleaned |  | ## X | 1705.2.1 |  |  | AISC 360 Table N5.4-3 |
| ii. Size, length, and location of welds | ## X |  | 1705.2.1 |  |  | AISC 360 Table N5.4-3 |
| iii. Welds meet visual acceptance criteria | ## X |  | 1705.2.1 |  |  | AISC 360 Table N5.4-3 |
| iv. Arc strikes | ## X |  | 1705.2.1 |  |  | AISC 360 Table N5.4-3 |
| v. K-area | ## X |  | 1705.2.1 |  |  | ## AISC 360 Table N5.4-3; ## When welding of doubler ## plates, continuity plates or stiffeners has been performed in the k-area, visually inspect the web k-area for cracks within ## 3 in. (75mm) of the weld. |
| vi. Backing removed and weld tabs removed (if required) | ## X |  | 1705.2.1 |  |  | AISC 360 Table N5.4-3 |
| vii. Repair activities | ## X |  | 1705.2.1 |  |  | AISC 360 Table N5.4-3 |
| viii. Document acceptance or rejection of welded joint or member | ## X |  | 1705.2.1 |  |  | AISC 360 Table N5.4-3 |
| d. Inspection Tasks Prior to Bolting |  |  | 1705.2.1 |  |  | ## AISC 360 Table N5.6-1 |
| i. Manufacturer’s certification available for fastener materials | ## X |  | 1705.2.1 |  |  | AISC 360 Table N5.6-1 |
| ii. Fasteners marked in accordance with ASTM requirements |  | ## X | 1705.2.1 |  |  | AISC 360 Table N5.6-1 |
| iii. Proper fasteners selected for the joint detail (grade, type, bolt length if threads are to be excluded from shear plane) |  | ## X | 1705.2.1 |  |  | AISC 360 Table N5.6-1 |
| iv. Proper bolting procedure selected for joint detail |  | ## X | 1705.2.1 |  |  | AISC 360 Table N5.6-1 |
| v. Connecting elements, including the appropriate faying surface condition and hole preparation, if specified, meet applicable requirements. |  | ## X | 1705.2.1 |  |  | AISC 360 Table N5.6-1 |
| vi. Pre-installation verification testing by installation personnel observed and documented for fastener assemblies and methods used. |  | ## X | 1705.2.1 |  |  | AISC 360 Table N5.6-1 |
| vii. Proper storage provided for bolts, nuts, washers and other fastener components. |  | ## X | 1705.2.1 |  |  | AISC 360 Table N5.6-1 |
| e. Inspection Tasks During Bolting |  |  | 1705.2.1 |  |  | ## AISC 360 Table N5.6-2 |
| i. Fastener assemblies, of suitable condition, placed in all holes and washers (if required) are positioned as required. |  | ## X | 1705.2.1 |  |  | ## AISC 360 Table N5.6-2 |
| ii. Joint brought to the snug-tight condition prior to the pretensioning operation. |  | ## X | 1705.2.1 |  |  | AISC 360 Table N5.6-2 |
| iii. Fastener component not turned by the wrench prevented from rotating. |  | ## X | 1705.2.1 |  |  | AISC 360 Table N5.6-2 |
| iv. Fasteners are pretensioned in accordance with the RCSC Specification, progressing systematically from the most rigid point toward the free edges. |  | ## X | 1705.2.1 |  |  | AISC 360 Table N5.6-2 |
| f. Inspection Tasks After Bolting |  |  | 1705.2.1 |  |  | ## AISC 360 Table N5.6-3 |
| i. Document acceptance or rejection of bolted connections. | ## X |  | 1705.2.1 |  |  | ## AISC 360 Table N5.6-3 |
| g. Inspection of Steel Elements of Composite Construction Prior to Concrete Placement |  |  | 1705.2.1 |  |  | ## AISC 360 Table N6.1 |
| i. Placement and installation of steel deck. | ## X |  | 1705.2.1 |  |  | AISC 360 Table N6.1 |
| ii. Placement and installation of steel headed stud anchors. | ## X |  | 1705.2.1 |  |  | AISC 360 Table N6.1 |
| iii. Document acceptance or rejection of steel elements | ## X |  | 1705.2.1 |  |  | AISC 360 Table N6.1 |
| 2. Cold-Formed Steel Deck |  |  | ## 1705.2.2 |  |  |  |
| a. Inspection or Execution Tasks prior to Deck Placement |  |  | 1705.2.2 |  |  | ## SDI QA/QC Table 1.1 |
| i. Verify compliance of materials (deck and all deck accessories) with construction documents, including profiles, material properties, and base metal thickness. | ## X |  | 1705.2.2 |  |  | SDI QA/QC Table 1.1 |
| ii. Document acceptance or rejection of deck and deck accessories. | ## X |  | 1705.2.2 |  |  | SDI QA/QC Table 1.1 |
| b. Inspection or Execution Tasks after Deck Placement |  |  |  |  |  | SDI QA/QC Table 1.2 |
| i. Verify compliance of deck and all deck accessories installation with construction documents. | ## X |  | 1705.2.2 |  |  | SDI QA/QC Table 1.2 |
| ii. Verify deck materials are represented by the mill certifications that comply with the construction documents. | ## X |  | 1705.2.2 |  |  | SDI QA/QC Table 1.2 |
| iii. Document acceptance or rejection of installation of deck and deck accessories. | ## X |  | 1705.2.2 |  |  | SDI QA/QC Table 1.2 |
| c. Inspection or Execution Tasks Prior to Welding |  |  | 1705.2.2 |  |  | SDI QA/QC Table 1.3 |
| i. Welding Procedure Specifications (WPS) available. |  | ## X | 1705.2.2 |  |  | SDI QA/QC Table 1.3 |
| ii. Manufacturer certifications for welding consumables available |  | ## X | 1705.2.2 |  |  | SDI QA/QC Table 1.3 |
| iii. Material identification (type/grade). |  | ## X | 1705.2.2 |  |  | SDI QA/QC Table 1.3 |
| iv. Check welding equipment. |  | ## X | 1705.2.2 |  |  | SDI QA/QC Table 1.3 |
| d. Inspection or Execution Tasks during Welding |  |  | 1705.2.2 |  |  | SDI QA/QC Table 1.4 |
| i. Use of qualified welders. |  | ## X | 1705.2.2 |  |  | SDI QA/QC Table 1.4 |
| ii. Control and handling of welding consumables. |  | ## X | 1705.2.2 |  |  | SDI QA/QC Table 1.4 |
| iii. Environmental conditions (wind speed, moisture, temperature). |  | ## X | 1705.2.2 |  |  | SDI QA/QC Table 1.4 |
| iv. Verify WPS followed. |  | ## X | 1705.2.2 |  |  | SDI QA/QC Table 1.4 |
| e. Inspection or Execution Tasks after Welding |  |  | 1705.2.2 |  |  | SDI QA/QC Table 1.5 |
| i. Verify size and location of welds, including support, sidelap, and perimeter welds. | ## X |  | 1705.2.2 |  |  | SDI QA/QC Table 1.5 |
| ii. Welds meet visual acceptance criteria. | ## X |  | 1705.2.2 |  |  | SDI QA/QC Table 1.5 |
| iii. Verify repair activities. | ## X |  | 1705.2.2 |  |  | SDI QA/QC Table 1.5 |
| iv. Document acceptance or rejection of welds. | ## X |  | 1705.2.2 |  |  | SDI QA/QC Table 1.5 |
| f. Inspection or Execution Tasks prior to Mechanical Fastening |  |  | 1705.2.2 |  |  | SDI QA/QC Table 1.6 |
| i. Manufacturer installation instructions available for mechanical fasteners. |  | ## X | 1705.2.2 |  |  | SDI QA/QC Table 1.6 |
| ii. Proper tools available for fastener installation. |  | ## X | 1705.2.2 |  |  | SDI QA/QC Table 1.6 |
| iii. Proper storage for mechanical fasteners. |  | ## X | 1705.2.2 |  |  | SDI QA/QC Table 1.6 |
| g. Inspection or Execution Tasks during Mechanical Fastening |  |  | 1705.2.2 |  |  | SDI QA/QC Table 1.7 |
| i. Fasteners are positioned as required. |  | ## X | 1705.2.2 |  |  | SDI QA/QC Table 1.7 |
| ii. Fasteners are installed in accordance with manufacturer’s instructions. |  | ## X | 1705.2.2 |  |  | SDI QA/QC Table 1.7 |
| h. Inspection or Execution Tasks after Mechanical Fastening |  |  | 1705.2.2 |  |  | SDI QA/QC Table 1.8 |
| i. Check spacing, type, and installation of support fasteners. | ## X |  | 1705.2.2 |  |  | SDI QA/QC Table 1.8 |
| ii. Check spacing, type, and installation of sidelap fasteners. | ## X |  | 1705.2.2 |  |  | SDI QA/QC Table 1.8 |
| iii. Check spacing, type, and installation of perimeter fasteners. | ## X |  | 1705.2.2 |  |  | SDI QA/QC Table 1.8 |
| iv. Verify repair activities. | ## X |  | 1705.2.2 |  |  | SDI QA/QC Table 1.8 |
| v. Document acceptance or rejection of mechanical fasteners. | ## X |  | 1705.2.2 |  |  | SDI QA/QC Table 1.8 |
| 3. Open-Web Steel Joists and Joist Girders |  |  | ## 1705.2.3 |  |  |  |
| a. Installation of open-web steel joists and joist girders |  | ## X | ## Table 1705.2.3 |  |  |  |
| i. End connections – welded or bolted. |  | ## X | Table 1705.2.3 |  |  | ## SJI Specifications listed in Section 2207.1. |
| ii. Bridging – Horizontal or diagonal. |  | ## X | Table 1705.2.3 |  |  |  |
| a. Standard bridging. |  | ## X | Table 1705.2.3 |  |  | ## SJI Specifications listed in Section 2207.1. |
| b. Bridging that differs from the SJI specifications listed in Section 2207.1 |  | ## X | Table 1705.2.3 |  |  |  |
| 4. Cold-Formed Steel Trusses spanning 60 feet or Greater |  | ## X | ## 1705.2.4 |  |  | ## The Special Inspector shall ## verify that the temporary restraint/bracing and the permanent individual truss member restraint/bracing are installed in accordance with the approved truss submittal ## package. |
| ## C. Concrete Construction |  |  | 1705.3 |  |  |  |
| 1. Inspect reinforcement, including prestressing tendons, and verify placement. |  | X | Table 1705.3 |  |  | ACI 318 Ch. 20, 25.2, 25.3, 26.6.1-26.6.3 IBC 1908.4 |
| 2 Reinforcing Bar Welding: |  | X | Table 1705.3 1705.3.1 |  |  | AWS D1.4, ACI 318: 26.6.4 |
| a. Verify weldability of reinforcing bars other than ASTM A706: |  | X | Table 1705.3 |  |  | AWS D1.4 ACI 318: 26.6.4 |
| b. Inspect single pass fillet welds, maximum 5/16”; and |  | X | Table 1705.3 |  |  | AWS D1.4 ACI 318: 26.6.4 |
| c. Inspect all other welds | X |  | Table 1705.3 |  |  | AWS D1.4 ACI 318: 26.6.4 |
| 3. Inspect anchors cast in concrete. |  | X | Table 1705.3 |  |  | ACI 318: 17.8.2 |
| 4. Inspect anchors post-installed in hardened concrete members. |  | X | Table 1705.3 |  |  |  |
| a. Adhesive anchors installed in horizontally or upwardly inclined orientations to resist sustained tension loads. | X |  | Table 1705.3 |  |  | ACI 318: 17.8.2.4 |
| b. Mechanical anchors and adhesive anchors not defined in item 4a. |  | X | Table 1705.3 |  |  | ACI 318: 17.8.2 |
| 5. Verify use of required design mix |  | X | Table 1705.3 |  |  | ACI 318: Ch. 19, 26.4.3, 26.4.4; IBC 1904.1, 1904.2, 1908.2, 1908.3 |
| 6. Prior to concrete placement, fabricate specimens for strength tests, perform slump and air content tests, and determine the temperature of concrete. | X |  | Table 1705.3 |  |  | ASTM C172, ASTM C31; ACI 318: 26.4, 26.12; IBC 1908.10 |
| 7. Inspect concrete and shotcrete placement for proper application techniques. | X |  | Table 1705.3 |  |  | ACI 318: 26.5; IBC 1908.6, 1908.7, 1908.8 |
| 8. Verify maintenance of specified curing temperature and techniques. |  | X | Table 1705.3 |  |  | ACI 318: 26.5.3-26.5.5 IBC: 1908.9 |
| 9. Inspect Prestressed concrete for: |  |  | Table 1705.3 |  |  |  |
| a. Application of prestressing forces; and | X |  | Table 1705.3 |  |  | ACI 318: 26.10 |
| b. Grouting of bonded prestressing tendons | X |  | Table 1705.3 |  |  | ACI 318: 26.10 |
| 10. Inspect erection of precast concrete members |  | X | Table 1705.3 |  |  | ACI 318: Ch. 26.8 |
| 11. Verify in-situ concrete strength, prior to stressing tendons in post-tensioned concrete and prior to removal of shores and forms from beams and structural slabs. |  | X | Table 1705.3 |  |  | ACI 318: 26.11.2 |
| 12. Inspect formwork for shape, location and dimensions of the concrete member being formed. |  | X | Table 1705.3 |  |  |  |
| ## D. Masonry Construction ## (Check LA, LB or ## LC below) LA = Level A Quality Assurance LB = Level B Quality Assurance LC = Level C Quality Assurance |  |  | 1705.4 |  |  | TMS 402/ACI530/ASCE5 TMS 602/ACI530.1/ASCE6 |
| Level A Quality Assurance: Minimum Verification |  |  |  |  |  |  |
| A1. Prior to construction, verify certificates of compliance used in masonry construction. |  | X |  |  |  | TMS 402/ACI530/ASCE5 Table 3.1.1 |
| Level B Quality Assurance: Minimum Special Inspections |  |  |  |  |  |  |
| B1. Verify Compliance with approved submittals. |  | X |  |  |  | TMS 402/ACI530/ASCE5 Table 3.1.2 |
| B2: As masonry construction begins, verify that the following are in compliance: |  |  |  |  |  | TMS 402/ACI530/ASCE5 Table 3.1.2 |
| B2a: Proportions of site-prepared mortar. |  | X |  |  |  | TMS 402/ACI530/ASCE5 Table 3.1.2 |
| B2b: Construction of Mortar Joints. |  | X |  |  |  | TMS 402/ACI530/ASCE5 Table 3.1.2 |
| B2c: Grade and size of prestressing tendons and anchorage. |  | X |  |  |  | TMS 402/ACI530/ASCE5 Table 3.1.2 |
| B2d: Location of reinforcement, connectors, and prestressing tendons and anchorage. |  | X |  |  |  | TMS 402/ACI530/ASCE5 Table 3.1.2 |
| B2e: Prestressing technique. |  | X |  |  |  | TMS 402/ACI530/ASCE5 Table 3.1.2 |
| B2f: Properties of thin bed mortar for AAC masonry. | X | X |  |  |  | TMS 402/ACI530/ASCE5 Table 3.1.2 Continuous inspection required for the first 5000sf of AAC Masonry, Periodic inspection is required after the first 5000sf of AAC masonry. |
| B3. Prior to grouting, verify that the following are in compliance: |  | X |  |  |  | TMS 402/ACI530/ASCE5 Table 3.1.2 |
| B3a: Grout space. |  | X |  |  |  | TMS 402/ACI530/ASCE5 Table 3.1.2 |
| B3b: Grade, type, and size of reinforcement and anchor bolts, and prestressing tendons and anchorage. |  | X |  |  |  | TMS 402/ACI530/ASCE5 Table 3.1.2 |
| B3c: Placement of reinforcement, connectors, and prestressing tendons and anchorage. |  | X |  |  |  | TMS 402/ACI530/ASCE5 Table 3.1.2 |
| B3d: Proportions of site-prepared grout for bonded tendons. |  | X |  |  |  | TMS 402/ACI530/ASCE5 Table 3.1.2 |
| B3e: Construction of mortar joints. |  | X |  |  |  | TMS 402/ACI530/ASCE5 Table 3.1.2 |
| B4: Verify during construction: |  | X |  |  |  | TMS 402/ACI530/ASCE5 Table 3.1.2 |
| B4a: Size and location of structural elements. |  | X |  |  |  | TMS 402/ACI530/ASCE5 Table 3.1.2 |
| B4b: Type, size and location of anchors, including other details of anchorage of masonry to structural members, frames, or other construction. |  | X |  |  |  | TMS 402/ACI530/ASCE5 Table 3.1.2 |
| B4c: Welding of reinforcement. | X |  |  |  |  | TMS 402/ACI530/ASCE5 Table 3.1.2 |
| B4d: Preparation, construction, and protection of masonry during cold weather (temperature below 40dF) or hot weather (temperature above 90dF) |  | X |  |  |  | TMS 402/ACI530/ASCE5 Table 3.1.2 |
| B4e: Application and measurement of prestressing force. | X |  |  |  |  | TMS 402/ACI530/ASCE5 Table 3.1.2 |
| B4f: Placement of grout and prestressing grout for bonded tendons is in compliance. | X |  |  |  |  | TMS 402/ACI530/ASCE5 Table 3.1.2 |
| B4g: Placement of AAC masonry units and construction of thin-bed mortar joints. | X | X |  |  |  | TMS 402/ACI530/ASCE5 Table 3.1.2 Continuous inspection required for the first 5000sf of AAC Masonry, Periodic inspection is required after the first 5000sf of AAC masonry. |
| B5: Observe preparation of grout specimens, mortar specimens, and/or prisms. |  | X |  |  |  | TMS 402/ACI530/ASCE5 Table 3.1.2 |
| Minimum Tests |  |  |  |  |  |  |
| B6: Verification of Slump flow and Visual Stability Index (VSI) as delivered to the project site in accordance with Specification Article 1.5B1.b.3 for self-consolidating grout. |  |  |  |  |  | TMS 402/ACI530/ASCE5 Table 3.1.2 |
| B7: Verification of f”m and f”aac in accordance with Specification Article 1.4B prior to construction, except where specifically exempted by this Code. |  |  |  |  |  | TMS 402/ACI530/ASCE5 Table 3.1.2 |
| Level C Quality Assurance: Minimum Special Inspections |  |  |  |  |  |  |
| C1. Verify compliance with the approved submittals. |  | X |  |  |  | TMS 402/ACI530/ASCE5 Table 3.1.3 |
| C2. Verify that the following are in compliance: |  |  |  |  |  | TMS 402/ACI530/ASCE5 Table 3.1.3 |
| C2a. Proportions of site mixed mortar, grout and prestressing grout for bonded tendons. |  | X |  |  |  | TMS 402/ACI530/ASCE5 Table 3.1.3 |
| C2b. Grade, type, and size of reinforcement and anchor bolts, and prestressing tendons and anchorages. |  | X |  |  |  | TMS 402/ACI530/ASCE5 Table 3.1.3 |
| C2c. Placement of masonry units and construction of mortar joints. |  | X |  |  |  | TMS 402/ACI530/ASCE5 Table 3.1.3 |
| C2d. Placement of reinforcement, connectors, and prestressing tendons and anchorages. | X |  |  |  |  | TMS 402/ACI530/ASCE5 Table 3.1.3 |
| C2e. Grout spacing prior to grouting. | X |  |  |  |  | TMS 402/ACI530/ASCE5 Table 3.1.3 |
| C2f. Placement of grout and prestressing grout for bonded tendons. | X |  |  |  |  | TMS 402/ACI530/ASCE5 Table 3.1.3 |
| C2g. Size and location of structural elements. |  | X |  |  |  | TMS 402/ACI530/ASCE5 Table 3.1.3 |
| C2h. Type, size, and location of anchors including other details of anchorage of masonry to structural members, frames, or other construction. | X |  |  |  |  | TMS 402/ACI530/ASCE5 Table 3.1.3 |
| C2i. Welding of reinforcement. | X |  |  |  |  | TMS 402/ACI530/ASCE5 Table 3.1.3 |
| C2j. Preparation, construction, and protection of masonry during cold weather (temperature below 40dF) or hot weather (temperature above 90dF). |  | X |  |  |  | TMS 402/ACI530/ASCE5 Table 3.1.3 |
| C2k. Application and measurement of prestressing force. | X |  |  |  |  | TMS 402/ACI530/ASCE5 Table 3.1.3 |
| C2l. Placement of AAC masonry units and construction of thin-bed mortar joints. | X |  |  |  |  | TMS 402/ACI530/ASCE5 Table 3.1.3 |
| C2m. Properties of thin-bed mortar for AAC masonry. | X |  |  |  |  | TMS 402/ACI530/ASCE5 Table 3.1.3 |
| C3. Observe preparation of grout specimens, mortar specimens, and/or prisms. | X |  |  |  |  | TMS 402/ACI530/ASCE5 Table 3.1.3 |
| Minimum Tests |  |  |  |  |  |  |
| D1. Verification of f”m and f’AAC in accordance with Specification Article 1.4B prior to construction and for every 5,000sf during construction. |  |  |  |  |  | TMS 402/ACI530/ASCE5 Table 3.1.3 |
| D2. Verification of proportions of materials in premixed or preblended mortar, prestressing grout, and grout other than self-consolidating grout, as delivered to the project site. |  |  |  |  |  | TMS 402/ACI530/ASCE5 Table 3.1.3 |
| D3. Verification of Slump flow and Visual Stability Index (VSI) as delivered to the project site in accordance with Specification Article 1.5B.1.b.3 for self-consolidating grout. |  |  |  |  |  | TMS 402/ACI530/ASCE5 Table 3.1.3 |
| ## E. Wood Construction |  |  | 1705.5 |  |  |  |
| 1. High Load Diaphragms |  | X | 1705.5.1 |  |  |  |
| 2. Metal Plate Connected Wood Trusses spanning 60 feet or Greater |  | X | 1705.5.2 |  |  |  |
| ## F. Soils |  |  | 1705.6 |  |  |  |
| 1. Verify materials below shallow foundations are adequate to achieve the design bearing capacity. |  | X | Table 1705.6 |  |  |  |
| 2. Verify excavations are extended to a proper depth and have reached proper material. |  | X | Table 1705.6 |  |  |  |
| 3. Perform classification and testing of compacted fill materials. |  | X | Table 1705.6 |  |  |  |
| 4. Verify use of proper materials, densities and lift thicknesses during placement and compaction of compacted fill. | X |  | Table 1705.6 |  |  |  |
| 5. Prior to placement of compacted fill, inspect subgrade and verify that site has been prepared properly. |  | X | Table 1705.6 |  |  |  |
| ## G. Driven Deep Foundations |  |  | 1705.7 |  |  |  |
| 1. Verify element materials, sizes and lengths, comply with the requirements. | X |  | Table 1705.7 |  |  |  |
| 2. Determine capacities of test elements and conduct additional load tests, as required. | X |  | Table 1705.7 |  |  |  |
| 3. Inspect driving operations and maintain complete and accurate records for each elements. | X |  | Table 1705.7 |  |  |  |
| 4. Verify placement locations and plumbness, confirm type and size of hammer, record number of blows per foot of penetration, determine required penetrations to achieve design capacity, record tip and butt elevations and document any damage to foundation element. | X |  | Table 1705.7 |  |  |  |
| 5. For steel elements, perform additional special inspections in accordance with Section 1705.2. | - | - | Table 1705.7 |  |  |  |
| 6. For concrete elements and concrete-filled elements, perform tests and additional special inspections in accordance with Section 1705.3. | - | - | Table 1705.7 |  |  |  |
| 7. For specialty elements, perform additional inspections as determined by the registered design professional in responsible charge. | - | - | Table 1705.7 |  |  |  |
| ## H. Cast-in-place Deep Foundations |  |  | 1705.8 |  |  |  |
| 1. Inspect drilling operations and maintain complete and accurate records for each element. | X |  | Table 1705.8 |  |  |  |
| 2. Verify placement locations and plumbness, confirm element diameters, bell diameters (if applicable), lengths, embedment into bedrock (if applicable) and adequate end-bearing strata capacity. Record concrete or grout volumes. | X |  | Table 1705.8 |  |  |  |
| 3. For concrete elements, perform tests and additional special inspections in accordance with Section 1705.3. | - | - | Table 1705.8 |  |  |  |
| ## I. Helical Pile Foundations | X |  | 1705.9 |  |  |  |
| ## J. Fabricated Items |  |  | 1704.2.5 1705.10 |  |  | Where fabrication of structural, load-bearing, or lateral load resisting members or assemblies is being conducted on the premises of a fabricators shop |
| 1. Structural Steel |  | X |  |  |  |  |
| 2. Steel Joists |  | X |  |  |  |  |
| 3. Precast Concrete |  | X |  |  |  |  |
| 4. Wood Construction |  | X |  |  |  |  |
| ## K. Special Inspections for Wind Resistance |  |  | 1705.11 |  |  | RDP to identify the main windforce-resisting systems and wind-resisting components that are subject to special inspection per BCNYS Section 1704.3.3. |
| 1. Structural Wood | X | X | 1705.11.1 |  |  | Inspection frequency varies depending on element inspection type. |
| 2. Cold Formed steel light framed Construction |  | X | 1705.11.2 |  |  |  |
| 3. Wind-resisting Components |  | X | 1705.11.3 |  |  |  |
| ## L. Special Inspections for Seismic Resistance |  |  | 1705.12 |  |  | RDP to identify the designated seismic systems and seismic force-resisting systems that are subject to special inspection per BCNYS Section 1704.3.2. |
| 1. Structural Steel |  | X | 1705.12.1 |  |  | AISC 341 Section J |
| 2. Structural Wood | X | X | 1705.12.2 |  |  | Inspection frequency varies depending on element inspection type. |
| 3. Cold Formed steel light framed Construction |  | X | 1705.12.3 |  |  |  |
| 4. Designated seismic systems | X | X | 1705.12.4 |  |  | ASCE 7 Section 13.2.2 Insepction frequency may vary based on project specific SDC. |
| 5. Architectural Components |  | X | 1705.12.5 |  |  |  |
| 6. Plumbing, Mechanical, and Electrical Components |  | X | 1705.12.6 |  |  |  |
| 7. Storage Racks |  | X | 1705.12.7 |  |  |  |
| 8. Seismic Isolation Systems |  | X | 1705.12.8 |  |  |  |
| 9. Cold Formedsteel special bolted moment frames |  | X | 1705.12.9 |  |  |  |
| ## M. Testing for Seismic Resistance |  |  | 1705.13 |  |  |  |
| 1. Structural Steel |  | X | 1705.13.1 |  |  |  |
| 2. Nonstructural Components |  | X | 1705.13.2 |  |  |  |
| 3. Designated Seismic Systems |  | X | 1705.13.3 |  |  |  |
| 4. Seismic Isolation Systems |  | X | 1705.13.4 |  |  |  |
| ## N. Sprayed Fire-Resistant Materials |  |  | 1705.14 |  |  |  |
| 1. Physical and visual tests |  | X | 1705.14.1 |  |  |  |
| 2. Structural Member Surface Conditions |  | X | 1705.14.2 |  |  |  |
| 3. Application |  | X | 1705.14.3 |  |  |  |
| 4. Thickness |  | X | 1705.14.4 |  |  |  |
| 5. Density |  | X | 1705.14.5 |  |  |  |
| 6. Bond Strength |  | X | 1705.14.6 |  |  |  |
| ## O. Mastic and Intumescent Fire-Resistant Coatings |  | X | 1705.15 |  |  |  |
| ## P. Exterior Insulation and Finish Systems (EIFS) |  |  | 1705.16 |  |  |  |
| 1. Exterior Insulation and Finish Systems (EIFS) |  | X | 1705.16 |  |  |  |
| 2. Water Resistive Barrier Coating |  | X | 1705.16.1 |  |  |  |
| ## Q. Fire-Resistant Penetrations and Joints |  |  | 1705.17 |  |  |  |
| 1. Penetration Firestops |  | X | 1705.17.1 |  |  |  |
| 2. Fire-resistant joint systems |  | X | 1705.17.2 |  |  |  |
| ## R. Testing for Smoke Control |  |  | 1705.18 |  |  |  |
| 1. Testing Scope |  | X | 1705.18.1 |  |  |  |
| 2. Qualifications |  | X | 1705.18.2 |  |  |  |
| ## S. Additional Special Inspections/Tests |  |  | The registered design professional of record shall identify if additional tests and inspections defined by BC Section 1705.1.1 are required and provide specific requirements below. |  |  |  |

NOTES:

- RDP to provide reference specification section detailing the requirements for inspections and/or tests and other clarifying notes, as necessary.

- Commentary/Notes by DASNY are provided for information only and are not intended to provide complete details of the required tests and inspections.  Refer to the Building Code of New York State for complete and detailed requirements.