	
	[image: image1.jpg]DASNY

YO RK




2025 NYS BUILDING CODE

STATEMENT OF SPECIAL INSPECTIONS



	BCNYS §1704.3 requires that the project Registered Design Professional in responsible charge prepare a Statement of Special Inspections.  Completion of this Statement of Special Inspections and submission to the Code Compliance Unit with the Construction Permit Application is a condition for issuance of the Construction Permit.  

	Campus/Facility:       

	Project Title:       

	Project #:       
	DASNY Project Manager:       

	Registered Design Professional (RDP):       

	Name of Person Completing Statement:       
	Phone:       
	Date:       

	Comments:       


	INSPECTIONS AND TESTS 

(Continuous & Periodic is 

as defined by the BCNYS)
	CONTINUOUS
	PERIODIC 
	BCNYS REFERENCE
	CHECK IF REQUIRED
	SPECIFICATION REFERENCE AND CLARIFYING NOTES
(by RDP)1
	COMMENTARY/NOTES and REFERENCE STANDARDS  (by DASNY)2

	A. Special Cases (Add requirements under Part U 

 as necessary)
	
	
	1705.1.1
	
	
	Special Inspections and  Tests shall be required for proposed work that is, in the opinion of   the building official, unusual in its nature.

	B. Steel Construction.
	
	
	1705.2
	
	
	

	1. Structural Steel and 

Stainless Steel
	
	
	1705.2.1
1705.2.2
	
	
	

	a.  Inspection tasks prior to welding;
	
	
	1705.2.1
1705.2.2
	
	
	AISC 360 Table N5.4-1
AISC 370 Table N5.4-1

	i.  Welder qualification records and continuity records
	
	
	1705.2.1

1705.2.2
	 FORMCHECKBOX 

	     
	AISC 360 Table N5.4-1

AISC 370 Table N5.4-1

	ii.  Welding procedure specifications (WPSs) available
	X
	
	1705.2.1
1705.2.2
	 FORMCHECKBOX 

	     
	AISC 360 Table N5.4-1
AISC 370 Table N5.4-1

	iii.  Manufacturer certifications for welding consumables available
	X
	
	1705.2.1
1705.2.2
	 FORMCHECKBOX 

	     
	AISC 360 Table N5.4-1
AISC 370 Table N5.4-1

	iv.  Material identification (type/grade)
	
	X
	1705.2.1
1705.2.2
	 FORMCHECKBOX 

	     
	AISC 360 Table N5.4-1

	v.  Welder identification system
	
	X
	1705.2.1
1705.2.2
	 FORMCHECKBOX 

	     
	AISC 360 Table N5.4-1
AISC 370 Table N5.4-1
The fabricator or erector, as applicable, shall maintain a system by which a welder who has welded a joint or member 
can be identified.  Die stamping of members subjected to fatigue shall be prohibited unless approved by the engineer of record.

	vi.  Fit up of groove welds (including joint geometry)
	
	X
	1705.2.1
1705.2.2
	 FORMCHECKBOX 

	     
	AISC 360 Table N5.4-1
AISC 370 Table N5.4-1

	vii.  Configuration and finish of access holes
	
	X
	1705.2.1
1705.2.2
	 FORMCHECKBOX 

	     
	AISC 360 Table N5.4-1

AISC 370 Table N5.4-1

	viii.  Fit-up of fillet welds
	
	X
	1705.2.1
1705.2.2
	 FORMCHECKBOX 

	     
	AISC 360 Table N5.4-1

AISC 370 Table N5.4-1

	ix.  Check Welding equipment
	
	X
	1705.2.1
1705.2.2
	 FORMCHECKBOX 

	     
	AISC 360 Table N5.4-1

AISC 370 Table N5.4-1

	b.  Inspection Tasks During Welding
	
	
	1705.2.1
1705.2.2
	
	
	AISC 360 Table N5.4-2

AISC 370 Table N5.4-2

	i.  Control and Handling of welding consumables.
	
	X
	1705.2.1
1705.2.2
	 FORMCHECKBOX 

	     
	AISC 360 Table N5.4-2

AISC 370 Table N5.4-2

	ii.  No welding over cracked tack welds.
	
	X
	1705.2.1
1705.2.2
	 FORMCHECKBOX 

	     
	AISC 360 Table N5.4-2

AISC 370 Table N5.4-2

	iii.  Environmental Conditions
	
	X
	1705.2.1
1705.2.2
	 FORMCHECKBOX 

	     
	AISC 360 Table N5.4-2

AISC 370 Table N5.4-2

	iv.  Verify WPS followed
	
	X
	1705.2.1
1705.2.2
	 FORMCHECKBOX 

	     
	AISC 360 Table N5.4-2

AISC 370 Table N5.4-2

	v.  Verify Welding Techniques
	
	X
	1705.2.1
1705.2.2
	 FORMCHECKBOX 

	     
	AISC 360 Table N5.4-2

AISC 370 Table N5.4-2

	vi.  Placement and installation of steel headed stud anchors
	X
	
	1705.2.1
1705.2.2
	 FORMCHECKBOX 

	     
	AISC 360 Table N5.4-2

AISC 370 Table N5.4-2

	c.  Inspection Tasks after Welding
	
	
	1705.2.1
1705.2.2
	
	
	AISC 360 Table N5.4-3

AISC 370 Table N5.4-3

	i.  Welds cleaned
	
	X
	1705.2.1
1705.2.2
	 FORMCHECKBOX 

	     
	AISC 360 Table N5.4-3

AISC 370 Table N5.4-3

	ii.  Size, length, and location of welds
	X
	
	1705.2.1
1705.2.2
	 FORMCHECKBOX 

	     
	AISC 360 Table N5.4-3

AISC 370 Table N5.4-3

	iii.  Welds meet visual acceptance criteria
	X
	 
	1705.2.1
1705.2.2
	 FORMCHECKBOX 

	     
	AISC 360 Table N5.4-3

AISC 370 Table N5.4-3

	iv.  Arc strikes
	X
	
	1705.2.1
1705.2.2
	 FORMCHECKBOX 

	     
	AISC 360 Table N5.4-3
AISC 370 Table N5.4-3

	v.  K-area
	X
	
	1705.2.1
1705.2.2
	 FORMCHECKBOX 

	     
	AISC 360 Table N5.4-3
AISC 370 Table N5.4-3
When welding of doubler 
plates, continuity plates or stiffeners has been performed in the k-area, visually inspect the web k-area for cracks within 
3 in. (75mm) of the weld.

	vi.  Weld access holes in rolled heavy shapes and built-up heavy shapes
	X
	
	1705.2.1
1705.2.2
	 FORMCHECKBOX 

	     
	AISC 360 Table N5.4-3
AISC 370 Table N5.4-3

	vii.  Backing removed and weld tabs removed (if required)
	X
	
	1705.2.1
1705.2.2
	 FORMCHECKBOX 

	     
	AISC 360 Table N5.4-3
AISC 370 Table N5.4-3

	viii.  Repair activities
	X
	
	1705.2.1
1705.2.2
	 FORMCHECKBOX 

	     
	AISC 360 Table N5.4-3
AISC 370 Table N5.4-3

	ix.  Document acceptance or rejection of welded joint or member
	X
	
	1705.2.1
1705.2.2
	 FORMCHECKBOX 

	     
	AISC 360 Table N5.4-3
AISC 370 Table N5.4-3

	x.  No prohibited welds have been added without the approval of the engineer of record
	
	X
	1705.2.1
1705.2.2
	 FORMCHECKBOX 

	     
	AISC 360 Table N5.4-3
AISC 370 Table N5.4-3

	d.  Inspection Tasks Prior to Bolting
	
	
	1705.2.1
1705.2.2
	
	
	AISC 360 Table N5.6-1
AISC 370 Table N5.6-1

	i.  Manufacturer’s certification available for fastener materials
	X
	
	1705.2.1
1705.2.2
	 FORMCHECKBOX 

	     
	AISC 360 Table N5.6-1
AISC 370 Table N5.6-1

	ii.  Fasteners marked in accordance with ASTM requirements
	
	X
	1705.2.1
1705.2.2
	 FORMCHECKBOX 

	     
	AISC 360 Table N5.6-1
AISC 370 Table N5.6-1

	iii.  Correct fasteners selected for the joint detail (grade, type, bolt length if threads are to be excluded from shear plane)
	
	X
	1705.2.1
1705.2.2
	 FORMCHECKBOX 

	     
	AISC 360 Table N5.6-1
AISC 370 Table N5.6-1

	iv.  Correct bolting procedure selected for joint detail
	
	X
	1705.2.1
1705.2.2
	 FORMCHECKBOX 

	     
	AISC 360 Table N5.6-1
AISC 370 Table N5.6-1

	v.  Connecting elements, including the appropriate faying surface condition and hole preparation, if specified, meet applicable requirements.
	
	X
	1705.2.1
1705.2.2
	 FORMCHECKBOX 

	     
	AISC 360 Table N5.6-1
AISC 370 Table N5.6-1

	vi.  Pre-installation verification testing by installation personnel observed and documented for fastener assemblies and methods used.
	
	X
	1705.2.1
1705.2.2
	 FORMCHECKBOX 

	     
	AISC 360 Table N5.6-1
AISC 370 Table N5.6-1

	vii.  Protected storage provided for bolts, nuts, washers and other fastener components.
	
	X
	1705.2.1
1705.2.2
	 FORMCHECKBOX 

	     
	AISC 360 Table N5.6-1
AISC 370 Table N5.6-1

	e.  Inspection Tasks During Bolting
	
	
	1705.2.1
1705.2.2
	
	
	AISC 360 Table N5.6-2
AISC 370 Table N5.6-2

	i.  Fastener assemblies placed in all holes, and washers and nuts are positioned as required.
	
	X
	1705.2.1
1705.2.2
	 FORMCHECKBOX 

	     
	AISC 360 Table N5.6-2
AISC 370 Table N5.6-2

	ii.  Joint brought to the snug-tight condition prior to the pretensioning operation.
	
	X
	1705.2.1
1705.2.2
	 FORMCHECKBOX 

	     
	AISC 360 Table N5.6-2
AISC 370 Table N5.6-2

	iii.  Fastener component not turned by the wrench prevented from rotating.
	
	X
	1705.2.1
1705.2.2
	 FORMCHECKBOX 

	     
	AISC 360 Table N5.6-2
AISC 370 Table N5.6-2

	iv.  Fasteners are pretensioned in accordance with the RCSC Specification, progressing systematically from the most rigid point toward the free edges.
	
	X
	1705.2.1
1705.2.2
	 FORMCHECKBOX 

	     
	AISC 360 Table N5.6-2
AISC 370 Table N5.6-2

	f.  Inspection Tasks After Bolting
	
	
	1705.2.1
1705.2.2
	
	
	AISC 360 Table N5.6-3

AISC 360 Table N5.6-3

	i.  Document acceptance or rejection of bolted connections.
	X
	
	1705.2.1
1705.2.2
	 FORMCHECKBOX 

	     
	AISC 360 Table N5.6-3

AISC 360 Table N5.6-3


	2.  Cold-Formed Steel Deck
	
	
	1705.2.3
	 FORMCHECKBOX 

	     
	

	a.  Inspection or Execution Tasks prior to Deck Placement
	
	
	1705.2.3
	
	
	SDI QA/QC Table 1.1

	i.  Verify compliance of materials (deck and all deck accessories) with construction documents, including profiles, material properties, and base metal thickness.
	X
	
	1705.2.3
	 FORMCHECKBOX 

	     
	SDI QA/QC Table 1.1

	ii.  Document acceptance or rejection of deck and deck accessories.
	X
	
	1705.2.3
	 FORMCHECKBOX 

	     
	SDI QA/QC Table 1.1

	b.  Inspection or Execution Tasks after Deck Placement
	
	
	
	
	
	SDI QA/QC Table 1.2

	i.  Verify compliance of deck and all deck accessories installation with construction documents.
	X
	
	1705.2.3
	 FORMCHECKBOX 

	     
	SDI QA/QC Table 1.2

	ii.  Verify deck materials are represented by the mill certifications that comply with the construction documents.
	X
	
	1705.2.3
	 FORMCHECKBOX 

	     
	SDI QA/QC Table 1.2

	iii.  Document acceptance or rejection of installation of deck and deck accessories.
	X
	
	1705.2.3
	 FORMCHECKBOX 

	     
	SDI QA/QC Table 1.2

	c.  Inspection or Execution Tasks Prior to Welding
	
	
	1705.2.3
	
	
	SDI QA/QC Table 1.3

	i.  Welding Procedure Specifications (WPS) available.
	
	X
	1705.2.3
	 FORMCHECKBOX 

	     
	SDI QA/QC Table 1.3

	ii.  Manufacturer certifications for welding consumables available
	
	X
	1705.2.3
	 FORMCHECKBOX 

	     
	SDI QA/QC Table 1.3

	iii.  Material identification (type/grade).
	
	X
	1705.2.3
	 FORMCHECKBOX 

	     
	SDI QA/QC Table 1.3

	iv.  Check welding equipment.
	
	X
	1705.2.3
	 FORMCHECKBOX 

	     
	SDI QA/QC Table 1.3

	d.  Inspection or Execution Tasks during Welding
	
	
	1705.2.3
	
	
	SDI QA/QC Table 1.4

	i.  Use of qualified welders.
	
	X
	1705.2.3
	 FORMCHECKBOX 

	     
	SDI QA/QC Table 1.4

	ii.  Control and handling of welding consumables.
	
	X
	1705.2.3
	 FORMCHECKBOX 

	     
	SDI QA/QC Table 1.4

	iii.  Environmental conditions (wind speed, moisture, temperature).
	
	X
	1705.2.3
	 FORMCHECKBOX 

	     
	SDI QA/QC Table 1.4

	iv.  Verify WPS followed.
	
	X
	1705.2.3
	 FORMCHECKBOX 

	     
	SDI QA/QC Table 1.4

	e.  Inspection or Execution Tasks after Welding
	
	
	1705.2.3
	
	
	SDI QA/QC Table 1.5

	i.  Verify size and location of welds, including support, sidelap, and perimeter welds.
	X
	
	1705.2.3
	 FORMCHECKBOX 

	     
	SDI QA/QC Table 1.5

	ii.  Welds meet visual acceptance criteria.
	X
	
	1705.2.3
	 FORMCHECKBOX 

	     
	SDI QA/QC Table 1.5

	iii.  Verify repair activities.
	X
	
	1705.2.3
	 FORMCHECKBOX 

	     
	SDI QA/QC Table 1.5

	iv.  Document acceptance or rejection of welds.
	X
	
	1705.2.3
	 FORMCHECKBOX 

	     
	SDI QA/QC Table 1.5

	f.  Inspection or Execution Tasks prior to Mechanical Fastening
	
	
	1705.2.3
	
	
	SDI QA/QC Table 1.6

	i.  Manufacturer installation instructions available for mechanical fasteners.
	
	X
	1705.2.3
	 FORMCHECKBOX 

	     
	SDI QA/QC Table 1.6

	ii.  Proper tools available for fastener installation.
	
	X
	1705.2.3
	 FORMCHECKBOX 

	     
	SDI QA/QC Table 1.6

	iii.  Proper storage for mechanical fasteners.
	
	X
	1705.2.3
	 FORMCHECKBOX 

	     
	SDI QA/QC Table 1.6

	g.  Inspection or Execution Tasks during Mechanical Fastening
	
	
	1705.2.3
	
	
	SDI QA/QC Table 1.7

	i.  Fasteners are positioned as required.
	
	X
	1705.2.3
	 FORMCHECKBOX 

	     
	SDI QA/QC Table 1.7

	ii.  Fasteners are installed in accordance with manufacturer’s instructions.
	
	X
	1705.2.3
	 FORMCHECKBOX 

	     
	SDI QA/QC Table 1.7

	h.  Inspection or Execution Tasks after Mechanical Fastening
	
	
	1705.2.3
	
	
	SDI QA/QC Table 1.8

	i.  Check spacing, type, and installation of support fasteners.
	X
	
	1705.2.3
	 FORMCHECKBOX 

	     
	SDI QA/QC Table 1.8

	ii.  Check spacing, type, and installation of sidelap fasteners.
	X
	
	1705.2.3
	 FORMCHECKBOX 

	     
	SDI QA/QC Table 1.8

	iii.  Check spacing, type, and installation of perimeter fasteners.
	X
	
	1705.2.3
	 FORMCHECKBOX 

	     
	SDI QA/QC Table 1.8

	iv.  Verify repair activities.
	X
	
	1705.2.3
	 FORMCHECKBOX 

	     
	SDI QA/QC Table 1.8

	v.  Document acceptance or rejection of mechanical fasteners.
	X
	
	1705.2.3
	 FORMCHECKBOX 

	     
	SDI QA/QC Table 1.8

	3.  Open-Web Steel Joists and Joist Girders
	
	
	1705.2.4
	
	
	

	a.  Installation of open-web steel joists and joist girders
	
	X
	Table 1705.2.4
	 FORMCHECKBOX 

	     
	

	i.  End connections – welded or bolted.
	
	X
	Table 1705.2.4
	 FORMCHECKBOX 

	     
	SJI Specifications listed in Section 2207.1.

	ii.  Bridging – Horizontal or diagonal.
	
	X
	Table 1705.2.4
	 FORMCHECKBOX 

	     
	

	a.  Standard bridging.
	
	X
	Table 1705.2.4
	 FORMCHECKBOX 

	     
	SJI Specifications listed in Section 2207.1.

	b.  Bridging that differs from the SJI specifications listed in Section 2207.1
	
	X
	Table 1705.2.4
	 FORMCHECKBOX 

	     
	

	4.  Cold-Formed Steel Trusses spanning 60 feet or Greater
	
	X
	1705.2.5
	 FORMCHECKBOX 

	     
	The Special Inspector shall 
verify that the temporary restraint/bracing and the permanent individual truss member restraint/bracing are installed in accordance with the approved truss submittal 
package.

	5.  Metal Building Systems
	
	X
	1705.2.6
	 FORMCHECKBOX 

	     
	The approved agency shall perform inspections of the 

erected metail building system

to verify compliance with the approved construction 

documents.

	a.  Installation of rafter/beam flange braces and column flange braces.
	
	X
	Table 1705.2.6
	 FORMCHECKBOX 

	     
	

	b.  Installation of purlins and girts, including specified lapping.
	
	X
	Table 1705.2.6
	 FORMCHECKBOX 

	     
	

	c.  Purlin and girt restraint/bridging/bracing.
	
	X
	Table 1705.2.6
	 FORMCHECKBOX 

	     
	

	d.  Installation of X-bracing, tightened to remove any sag.
	
	X
	Table 1705.2.6
	 FORMCHECKBOX 

	     
	

	C. Concrete Construction
	
	
	1705.3
	
	
	


	1.  Inspect reinforcement, including prestressing tendons, and verify placement.
	
	X
	Table 1705.3
	 FORMCHECKBOX 

	     
	ACI 318 Ch. 20, 25.2, 25.3, 26.6.1-26.6.3



	2  Reinforcing Bar Welding:
	
	
	Table 1705.3 
	 FORMCHECKBOX 

	     
	AWS D1.4, ACI 318:  26.6.4

	a.  Verify weldability of reinforcing bars other than ASTM A706: 
	
	X
	Table 1705.3
	 FORMCHECKBOX 

	     
	AWS D1.4

ACI 318:  26.13.1.4

	b.  Inspect welding of reinforcement for special moment frames, boundary elements of special structural walls and coupling beams. 
	X
	
	Table 1705.3
	 FORMCHECKBOX 

	     
	AWS D1.4

ACI 318:  26.13.3

	c.  Inspect welded reinforcement splices. 
	X
	
	Table 1705.3
	 FORMCHECKBOX 

	     
	

	d.  Inspect welding of primary tension reinforcement in corbels. 
	X
	
	Table 1705.3
	 FORMCHECKBOX 

	     
	

	e.  Inspect single pass fillet welds, maximum 5/16”; and
	
	X
	Table 1705.3
	 FORMCHECKBOX 

	     
	AWS D1.4

ACI 318:  26.13.3

	f.  Inspect all other welds
	
	X
	Table 1705.3
	 FORMCHECKBOX 

	     
	AWS D1.4

ACI 318:  26.13.3

	3.  Inspect anchors cast in concrete.
	
	X
	Table 1705.3
	 FORMCHECKBOX 

	     
	ACI 318:  26.13.3.3

	4.  Inspect anchors post-installed in hardened concrete members.
	
	X
	Table 1705.3
	 FORMCHECKBOX 

	     
	Table 1705.3 Note b

	a.  Adhesive anchors installed in horizontally or upwardly inclined orientations to resist sustained tension loads.


	X
	
	Table 1705.3
	 FORMCHECKBOX 

	     
	ACI 318:  26.13.3.2

	b.  Mechanical anchors and adhesive anchors not defined in item 4a.
	
	X
	Table 1705.3
	 FORMCHECKBOX 

	     
	ACI 318:  26.13.3

	5.  Verify use of required design mix
	
	X
	Table 1705.3
	 FORMCHECKBOX 

	     
	ACI 318:  Ch. 19, 26.4.3, 26.4.4; 

BCNYS 1904.1, 1904.2

	6.  Prior to concrete placement, fabricate specimens for strength tests, perform slump and air content tests, and determine the temperature of concrete.
	X
	
	Table 1705.3
	 FORMCHECKBOX 

	     
	ASTM C31, ASTM C172, 

ACI 318:  26.5, 26.12

	7.  Inspect concrete and shotcrete placement for proper application techniques.
	X
	
	Table 1705.3
	 FORMCHECKBOX 

	     
	ACI 318:  26.5

	8.  Verify maintenance of specified curing temperature and techniques.
	
	X
	Table 1705.3
	 FORMCHECKBOX 

	     
	ACI 318:  26.5.3-26.5.5

	9.  Inspect Prestressed concrete for:
	
	
	Table 1705.3
	
	
	

	a.  Application of prestressing forces
	X
	
	Table 1705.3
	 FORMCHECKBOX 

	     
	ACI 318:  26.10

	b.  Grouting of bonded prestressing tendons
	X
	
	Table 1705.3
	 FORMCHECKBOX 

	     
	ACI 318:  26.10

	10.  Inspect erection of precast concrete members
	
	X
	Table 1705.3
	 FORMCHECKBOX 

	     
	ACI 318:  Ch. 26.9

	11.  For precast concrete diaphragm connections or reinforcement at joints classified as moderate or high deformability elements (MDE or HDE) in structures assigned to Seismic Design Category C, D, E, or F, inspect such connections and reinforcement in the field for:
	
	
	Table 1705.3
	 FORMCHECKBOX 

	     
	ACI 318:  Ch. 26.13.1.3

ACI 550.5

	a.  Installation of the embedded parts.
	X
	
	Table 1705.3
	 FORMCHECKBOX 

	     
	ACI 318:  Ch. 26.13.1.3

ACI 550.5

	b.  Completion of the continuity of reinforcement across joints.
	X
	
	Table 1705.3
	 FORMCHECKBOX 

	     
	ACI 318:  Ch. 26.13.1.3

ACI 550.5

	c.  Completion of the connections in the field.
	X
	
	Table 1705.3
	 FORMCHECKBOX 

	     
	ACI 318:  Ch. 26.13.1.3

ACI 550.5

	12.  Inspect erection of precast concrete members
	
	X
	Table 1705.3
	 FORMCHECKBOX 

	     
	ACI 318:  Ch. 26.9

	13.  Verify in-situ concrete strength, prior to stressing tendons in post-tensioned concrete and prior to removal of shores and forms from beams and structural slabs.
	
	X
	Table 1705.3
	 FORMCHECKBOX 

	     
	ACI 318:  26.11.2

	14.  Inspect formwork for shape, location and dimensions of the concrete member being formed.
	
	X
	Table 1705.3
	 FORMCHECKBOX 

	     
	ACI 318:  26.11.1.2(b)

	D.  Masonry Construction

(Check L1, L2 or L3 below)

 FORMCHECKBOX 
  L1 = Level 1 Quality Assurance

 FORMCHECKBOX 
  L2 = Level 2 Quality Assurance

 FORMCHECKBOX 
  L3 = Level 3 Quality Assurance


	
	
	1705.4
	
	
	TMS 402/602

	Level 1 Quality Assurance:

Minimum Verification
	
	
	1705.4
	
	
	

	1.  Prior to construction, verification of compliance submittals.
	X
	
	1705.4
	 FORMCHECKBOX 

	     
	TMS 602 Table 3

TMS 602 Article 1.5


	Level 1 Quality Assurance:

Minimum Special Inspection Requirements
	
	
	1705.4
	
	
	

	1.  Type, Size, and location of veneer ties & movement joints
	
	X
	1705.4
	 FORMCHECKBOX 

	     
	TMS 602 Table 4

TMS 402 Section 13.2

TMS 602 Article 3.4E

Periodic inspection of veneers is required when the height of the veneer exceeds 60 feet above grade plane.

	2.  Installation of adhered veneer.
	
	X
	1705.4
	 FORMCHECKBOX 

	     
	TMS 602 Table 4

TMS 402 Section 13.3

TMS 602 Article 3.3D

Periodic inspection of veneers is required when the height of the veneer exceeds 60 feet above grade plane.

	Level 2 Quality Assurance:

Minimum Verification
	
	
	
	
	
	

	1.  Prior to construction, verification of compliance submittals.
	X
	
	1705.4
	 FORMCHECKBOX 

	     
	TMS 602 Table 3

TMS 602 Article 1.5



	2:  Prior to construction, verification of f’m and f’aac, except where specifically exempted by the Code.
	X
	
	1705.4
	 FORMCHECKBOX 

	     
	TMS 602 Table 3

TMS 602 Article 1.4B



	3.  During construction, verification of Slump flow and Visual Stability Index (VSI) when self-consolidating grout is delivered to the project site.
	X
	
	1705.4
	 FORMCHECKBOX 

	     
	TMS 602 Table 3

TMS 602 Article 1.5 & 1.6.3



	Level 2 Quality Assurance:

Minimum Special Inspection Requirements
	
	
	1705.4
	
	
	

	1.  As masonry construction begins, verify that the following are in compliance:
	
	
	1705.4
	
	
	TMS 602 Table 4

	a.  Proportions of site-prepared mortar.
	
	X
	1705.4
	 FORMCHECKBOX 

	     
	TMS 602 Table 4

TMS 602 Article 2.1 & 
2.6 A&C

	b.  Grade and size of prestressing tendons and anchorages.
	
	X
	1705.4
	 FORMCHECKBOX 

	     
	TMS 602 Table 4

TMS 602 Article 2.4B & 

2.4 K&L

	c:  Grade type and size of reinforcement, connectors, and anchor bolts.
	
	X
	1705.4
	 FORMCHECKBOX 

	     
	TMS 602 Table 4

TMS 602 Article 2.4A, D, E, F, G, I, & J

	d.  Prestressing technique.
	
	X
	1705.4
	 FORMCHECKBOX 

	     
	TMS 602 Table 4

TMS 602 Article 3.6B

	e.  Properties of thin-bed mortar for AAC masonry.
	X
	X
	1705.4
	 FORMCHECKBOX 

	     
	TMS 602 Table 4

TMS 602 Article 2.1 DC.1

Continuous inspection for first 5000 square feet, Periodic inspection after first 5000 

square feet of AAC masonry.

	f.  Sample panel construction.
	
	X
	1705.4
	 FORMCHECKBOX 

	     
	TMS 602 Table 4

TMS 602 Article 1.6D

	2.  Prior to grouting, verify that the following are in compliance:
	
	
	1705.4
	
	
	TMS 602 Table 4

	a:  Grout space.
	
	X
	1705.4
	 FORMCHECKBOX 

	     
	TMS 602 Table 4

TMS 602 Article 3.2D & 3.2F

	b:  Placement of prestressing tendons and anchorage.
	
	X
	1705.4
	 FORMCHECKBOX 

	     
	TMS 602 Table 4

TMS 402 Section 10.8 & 10.9

TMS 602 Article 3.6

	c:  Placement of reinforcement, connectors, and anchor bolts.
	
	X
	1705.4
	 FORMCHECKBOX 

	     
	TMS 602 Table 4

TMS 402 Section 6.1, 6.3.1, 6.3.6, & 6.3.7

TMS 602 Article 3.2E & 3.4

	d:  Proportions of site-prepared grout and prestressing grout for bonded tendons.
	
	X
	1705.4
	 FORMCHECKBOX 

	     
	TMS 602 Table 4

TMS 602 Article 2.6B & 

2.4K.1.b

	3:  Verify compliance of the following during construction:
	
	
	1705.4
	
	
	TMS 602 Table 4

	a.  Materials and procedures with the approved submittals.
	
	X
	1705.4
	 FORMCHECKBOX 

	     
	TMS 602 Table 4

TMS 602 Article 1.5

	b.  Placement of masonry unties and mortar joint construction.
	
	X
	1705.4
	 FORMCHECKBOX 

	     
	TMS 602 Table 4

TMS 602 Article 3.3B

	c.  Size and location of structural members.
	
	X
	1705.4
	 FORMCHECKBOX 

	     
	TMS 602 Table 4

TMS 602 Article 3.3G

	d.  Type, size, and location of anchors, including other details of anchorage of masonry to structural members, frames, or other construction.
	
	X
	1705.4
	 FORMCHECKBOX 

	     
	TMS 602 Table 4

TMS 402 Section 1.2.1(e), 6.2.1, & 6.3.1

	e.  Type, size, and location of veneer ties & movement joints.
	
	X
	1705.4
	 FORMCHECKBOX 

	     
	TMS 602 Table 4

TMS 402 Section 13.2

TMS 602 Article 3.4E

Periodic inspection of veneers is required when the height of the veneer exceeds 60 feet above grade plane.

	f.  Installation of adhered veneer.
	X
	
	1705.4
	 FORMCHECKBOX 

	     
	TMS 602 Table 4

TMS 402 Section 13.3

TMS 602 Article 3.3D

Periodic inspection of veneers is required when the height of the veneer exceeds 60 feet above grade plane.

	g.  Welding of reinforcement.
	X
	
	1705.4
	 FORMCHECKBOX 

	     
	TMS 602 Table 4

TMS 402 Section 6.1.7.3

	h.  Preparation, construction, and protection of masonry during cold weather (temperature below 40dF (4.4dC)) or hot weather (temperature above 90dF (32.2dC)).
	
	X
	1705.4
	 FORMCHECKBOX 

	     
	TMS 602 Table 4

TMS 602 Article 1.8 C&D

	i.  Application and measurement of prestressing force.
	X
	
	1705.4
	 FORMCHECKBOX 

	     
	TMS 602 Table 4

TMS 602 Article 3.6B

	j.  Placement of grout.
	X
	
	1705.4
	 FORMCHECKBOX 

	     
	TMS 602 Table 4

TMS 602 Article 3.5

	k.  Placement of prestressing grout for bonded tendons.
	X
	
	1705.4
	 FORMCHECKBOX 

	     
	TMS 602 Table 4

TMS 602 Article 3.6C

	l.  Placement of AAC masonry units and construction of thin-bed mortar joints.
	X
	X
	1705.4
	 FORMCHECKBOX 

	     
	TMS 602 Table 4

TMS 602 Article 3.3 B.8 & 

3.3 G.1.b

Continuous inspection for first 5000 square feet, Periodic inspection after first 5000 

square feet of AAC masonry.

	4.  Observe preparation of grout specimens, mortar specimens, and/or prisms.
	
	X
	1705.4
	 FORMCHECKBOX 

	     
	TMS 602 Table 4

TMS 602 Article 1.4 B.2.a.3, B.2.b.3, B.2.c.3, B.3, & B.4.

	Level 3 Quality Assurance:

Minimum Verification
	
	
	
	
	
	

	1.  Prior to construction, verification of compliance submittals.
	X
	
	1705.4
	 FORMCHECKBOX 

	     
	TMS 602 Table 3

TMS 602 Article 1.5



	2:  Prior to construction, verification of f’m and f’aac, except where specifically exempted by the Code.
	X
	
	1705.4
	 FORMCHECKBOX 

	     
	TMS 602 Table 3

TMS 602 Article 1.4B



	3.  During construction, verification of Slump flow and Visual Stability Index (VSI) when self-consolidating grout is delivered to the project site.
	X
	
	1705.4
	 FORMCHECKBOX 

	     
	TMS 602 Table 3

TMS 602 Article 1.5 & 1.6.3



	4.  During construction, verification of f’m and f’aac for every 5,000 square feet.
	X
	
	1705.4
	 FORMCHECKBOX 

	     
	TMS 602 Table 3

TMS 602 Article 1.4B



	5.  During construction, verification of proportions of materials as delivered to the project site for premixed or preblended mortar, prestressing grout, and grout other than self-consolidating grout.
	X
	
	1705.4
	 FORMCHECKBOX 

	     
	TMS 602 Table 3

TMS 602 Article 1.4 B



	Level 3 Quality Assurance:

Minimum Special Inspection Requirements
	
	
	1705.4
	
	
	

	1.  As masonry construction begins, verify that the following are in compliance:
	
	
	1705.4
	
	
	TMS 602 Table 4

	a.  Proportions of site-prepared mortar.
	
	X
	1705.4
	 FORMCHECKBOX 

	     
	TMS 602 Table 4

TMS 602 Article 2.1 & 

2.6 A&C

	b.  Grade and size of prestressing tendons and anchorages.
	
	X
	1705.4
	 FORMCHECKBOX 

	     
	TMS 602 Table 4

TMS 602 Article 2.4B & 

2.4 K&L

	c:  Grade type and size of reinforcement, connectors, and anchor bolts.
	
	X
	1705.4
	 FORMCHECKBOX 

	     
	TMS 602 Table 4

TMS 602 Article 2.4A, D, E, F, G, I, & J

	d.  Prestressing technique.
	
	X
	1705.4
	 FORMCHECKBOX 

	     
	TMS 602 Table 4

TMS 602 Article 3.6B

	e.  Properties of thin-bed mortar for AAC masonry.
	X
	
	1705.4
	 FORMCHECKBOX 

	     
	TMS 602 Table 4

TMS 602 Article 2.1 DC.1

	f.  Sample panel construction.
	X
	
	1705.4
	 FORMCHECKBOX 

	     
	TMS 602 Table 4

TMS 602 Article 1.6D

	2.  Prior to grouting, verify that the following are in compliance:
	
	
	1705.4
	
	
	TMS 602 Table 4

	a:  Grout space.
	X
	
	1705.4
	 FORMCHECKBOX 

	     
	TMS 602 Table 4

TMS 602 Article 3.2D & 3.2F

	b:  Placement of prestressing tendons and anchorage.
	
	X
	1705.4
	 FORMCHECKBOX 

	     
	TMS 602 Table 4

TMS 402 Section 10.8 & 10.9

TMS 602 Article 3.6

	c:  Placement of reinforcement, connectors, and anchor bolts.
	X
	
	1705.4
	 FORMCHECKBOX 

	     
	TMS 602 Table 4

TMS 402 Section 6.1, 6.3.1, 6.3.6, & 6.3.7

TMS 602 Article 3.2E & 3.4

	d:  Proportions of site-prepared grout and prestressing grout for bonded tendons.
	
	X
	1705.4
	 FORMCHECKBOX 

	     
	TMS 602 Table 4

TMS 602 Article 2.6B & 

2.4K.1.b

	3:  Verify compliance of the following during construction:
	
	
	1705.4
	
	
	TMS 602 Table 4

	a.  Materials and procedures with the approved submittals.
	
	X
	1705.4
	 FORMCHECKBOX 

	     
	TMS 602 Table 4

TMS 602 Article 1.5

	b.  Placement of masonry unties and mortar joint construction.
	
	X
	1705.4
	 FORMCHECKBOX 

	     
	TMS 602 Table 4

TMS 602 Article 3.3B

	c.  Size and location of structural members.
	
	X
	1705.4
	 FORMCHECKBOX 

	     
	TMS 602 Table 4

TMS 602 Article 3.3G

	d.  Type, size, and location of anchors, including other details of anchorage of masonry to structural members, frames, or other construction.
	X
	
	1705.4
	 FORMCHECKBOX 

	     
	TMS 602 Table 4

TMS 402 Section 1.2.1(e), 6.2.1, & 6.3.1

	e.  Welding of reinforcement.
	X
	
	1705.4
	 FORMCHECKBOX 

	     
	TMS 602 Table 4

TMS 402 Section 6.1.7.3

	f.  Preparation, construction, and protection of masonry during cold weather (temperature below 40dF (4.4dC)) or hot weather (temperature above 90dF (32.2dC)).
	
	X
	1705.4
	 FORMCHECKBOX 

	     
	TMS 602 Table 4

TMS 602 Article 1.8 C&D

	g.  Application and measurement of prestressing force.
	X
	
	1705.4
	 FORMCHECKBOX 

	     
	TMS 602 Table 4

TMS 602 Article 3.6B

	h.  Placement of grout.
	X
	
	1705.4
	 FORMCHECKBOX 

	     
	TMS 602 Table 4

TMS 602 Article 3.5

	i.  Placement of prestressing grout for bonded tendons.
	X
	
	1705.4
	 FORMCHECKBOX 

	     
	TMS 602 Table 4

TMS 602 Article 3.6C

	j.  Placement of AAC masonry units and construction of thin-bed mortar joints.
	X
	
	1705.4
	 FORMCHECKBOX 

	     
	TMS 602 Table 4

TMS 602 Article 3.3 B.8 & 

3.3 G.1.b

	4.  Observe preparation of grout specimens, mortar specimens, and/or prisms.
	X
	
	1705.4
	 FORMCHECKBOX 

	     
	TMS 602 Table 4

TMS 602 Article 1.4 B.2.a.3, B.2.b.3, B.2.c.3, B.3, & B.4.

	E. Wood Construction
	
	
	1705.5
	
	
	

	1.  High Load Diaphragms
	
	X
	1705.5.1
	 FORMCHECKBOX 

	     
	

	2.  Metal Plate Connected Wood Trusses spanning 60 feet or Greater
	
	X
	1705.5.2
	 FORMCHECKBOX 

	     
	

	3.  Mass Timber Construction
	
	X
	1705.5.3
	 FORMCHECKBOX 

	     
	

	a.  Inspection of anchorage and connections of mass timber construction to timber deep foundation systems
	
	X
	1705.5.3
	 FORMCHECKBOX 

	     
	

	b.  Inspect erection of mass timber construction
	
	X
	1705.5.3
	 FORMCHECKBOX 

	     
	

	c.  Inspection of connections where installation methods are required to meet design loads
	
	X
	1705.5.3
	 FORMCHECKBOX 

	     
	

	i.  Threaded Fasteners
	
	X
	1705.5.3
	 FORMCHECKBOX 

	     
	

	a.  Verify use of proper installation equipment.
	
	X
	1705.5.3
	 FORMCHECKBOX 

	     
	

	b.  Verify use of pre-drilled holes where required.
	
	X
	1705.5.3
	 FORMCHECKBOX 

	     
	

	c.  Inspect screws, including diameter, length, head type, spacing, installation angle and depth.
	
	X
	1705.5.3
	 FORMCHECKBOX 

	     
	

	ii.  Adhesive anchors installed in horizontal or upwardly inclined orientation to resist sustained tension loads.
	X
	
	1705.5.3
	 FORMCHECKBOX 

	     
	

	iii.  Adhesive anchors not defined in preceding cell.
	
	X
	1705.5.3
	 FORMCHECKBOX 

	     
	

	iv.  Bolted connections.
	
	X
	1705.5.3
	 FORMCHECKBOX 

	     
	

	v.  Concealed connections.
	
	X
	1705.5.3
	 FORMCHECKBOX 

	     
	

	F. Soils
	
	
	1705.6
	
	
	

	1.  Verify materials below shallow foundations are adequate to achieve the design bearing capacity.
	
	X
	Table 1705.6
	 FORMCHECKBOX 

	     
	

	2.  Verify excavations are extended to a proper depth and have reached proper material.
	
	X
	Table 1705.6
	 FORMCHECKBOX 

	     
	

	3.  Perform classification and testing of compacted fill materials.
	
	X
	Table 1705.6
	 FORMCHECKBOX 

	     
	

	4.  During fill placement,, verify use of proper materials and procedures in accordance with the provisions of the approved geotechnical report.  Verify densities and lift thicknesses during placement and compaction of compacted fill.
	X
	
	Table 1705.6
	 FORMCHECKBOX 

	     
	

	5.  Prior to placement of compacted fill, inspect subgrade and verify that site has been prepared properly.
	
	X
	Table 1705.6
	 FORMCHECKBOX 

	     
	

	G. Driven Deep Foundations
	
	
	1705.7
	
	
	

	1.  Verify element materials, sizes and lengths, comply with the requirements.
	X
	
	Table 1705.7
	 FORMCHECKBOX 

	     
	

	2.  Determine capacities of test elements and conduct additional load tests, as required.
	X
	
	Table 1705.7
	 FORMCHECKBOX 

	     
	

	3.  Inspect driving operations and maintain complete and accurate records for each elements.
	X
	
	Table 1705.7
	 FORMCHECKBOX 

	     
	

	4.  Verify placement locations and plumbness, confirm type and size of hammer, record number of blows per foot of penetration, determine required penetrations to achieve design capacity, record tip and butt elevations and document any damage to foundation element.
	X
	
	Table 1705.7
	 FORMCHECKBOX 

	     
	

	5.  For steel elements, perform additional special inspections in accordance with Section 1705.2.
	-
	-
	Table 1705.7
	 FORMCHECKBOX 

	     
	Frequency in accordance with BCNYS Section 1705.2.

	6.  For concrete elements and concrete-filled elements, perform tests and additional special inspections in accordance with Section 1705.3.
	-
	-
	Table 1705.7
	 FORMCHECKBOX 

	     
	Frequency in accordance with BCNYS Section 1705.3.

	7.  For specialty elements, perform additional inspections as determined by the registered design professional in responsible charge.
	-
	-
	Table 1705.7
	 FORMCHECKBOX 

	     
	Frequency in accordance with direction from the Registered Design Professional indicated on the Statement of Special Inspections.

	H. Cast-in-place Deep Foundations
	
	
	1705.8
	
	
	

	1.  Inspect drilling operations and maintain complete and accurate records for each element.
	X
	
	Table 1705.8
	 FORMCHECKBOX 

	     
	

	2.  Verify placement locations and plumbness, confirm element diameters, bell diameters (if applicable), lengths, embedment into bedrock (if applicable) and adequate end-bearing strata capacity.  Record concrete or grout volumes.
	X
	
	Table 1705.8
	 FORMCHECKBOX 

	     
	

	3.  For concrete elements, perform tests and additional special inspections in accordance with Section 1705.3.
	-
	-
	Table 1705.8
	 FORMCHECKBOX 

	     
	BCNYS Section 1705.3

	I. Helical Pile Foundations
	X
	
	1705.9
	
	
	

	J. Structural Integrity of    Deep Foundation Elements
	X
	
	1705.10
	
	
	Engineering assessment and testing required where there is a reasonable doubt as to the structural integrity of a deep foundation element.



	K. Fabricated Items
	
	 
	1704.2.5

1705.11


	
	
	Where fabrication of structural, load-bearing, or lateral load resisting members or assemblies is being conducted on the premises of a fabricators shop



	1.  Structural Steel
	
	X
	
	 FORMCHECKBOX 

	     
	

	2.  Steel Joists
	
	X
	
	 FORMCHECKBOX 

	     
	

	3.  Precast Concrete
	
	X
	
	 FORMCHECKBOX 

	     
	

	4.  Wood Construction
	
	X
	
	 FORMCHECKBOX 

	     
	

	L. Special Inspections for Wind Resistance
	
	
	1705.12
	
	
	RDP to identify the main windforce-resisting systems and wind-resisting components that are subject to special inspection per BCNYS Section 1704.3.3.

	1.  Structural Wood
	X
	X
	1705.12.1
	 FORMCHECKBOX 

	     
	Inspection frequency varies depending on element inspection type.

	2.  Cold Formed steel light framed Construction
	
	X
	1705.12.2
	 FORMCHECKBOX 

	     
	

	3.  Wind-resisting Components
	
	X
	1705.12.3
	 FORMCHECKBOX 

	     
	

	M. Special Inspections for Seismic Resistance
	
	
	1705.13
	
	
	RDP to identify the designated seismic systems and seismic force-resisting systems that are subject to special inspection per BCNYS Section 1704.3.2.

	1.  Structural Steel
	
	X
	1705.13.1
	 FORMCHECKBOX 

	     
	AISC 341 Section J

	2.  Structural Wood
	X
	X
	1705.13.2
	 FORMCHECKBOX 

	     
	Inspection frequency varies depending on element inspection type.

	3.  Cold-Formed steel light- frame Construction
	
	X
	1705.13.3
	 FORMCHECKBOX 

	     
	

	4.  Designated seismic systems
	X
	X
	1705.13.4
	 FORMCHECKBOX 

	     
	ASCE 7 Section 13.2.2

Insepction frequency may vary based on project specific SDC.

	5.  Architectural Components
	
	X
	1705.13.5
	 FORMCHECKBOX 

	     
	

	6.  Plumbing, Mechanical, and Electrical Components
	
	X
	1705.13.6
	 FORMCHECKBOX 

	     
	

	7.  Storage Racks
	
	X
	1705.13.7
	 FORMCHECKBOX 

	     
	Applicable to storage racks 8   feet in height or greater and assigned to Seismic Design Category D, E, F

Table 1705.13.7 

	a.  Materials used, to verify compliance with one or more of the material test reports in accordance with the approved construction documents.
	
	X
	1705.13.7
	 FORMCHECKBOX 

	     
	

	b.  Fabricated storage rack elements.
	
	X
	1705.13.7
	 FORMCHECKBOX 

	     
	BCNYS Section 1704.2.5

	c.  Storage rack anchorage installation.
	
	X
	1705.13.7
	 FORMCHECKBOX 

	     
	ANSI/MH16.1 Section 7.3.2

	d.  Completed storage rack system, to indicate compliance with the approved construction documents.
	
	X
	1705.13.7
	 FORMCHECKBOX 

	     
	

	8.  Seismic Isolation Systems
	
	X
	1705.13.8
	 FORMCHECKBOX 

	     
	

	9.  Cold Formed steel special bolted moment frames
	
	X
	1705.13.9
	 FORMCHECKBOX 

	     
	

	N. Testing for Seismic Resistance
	
	
	1705.14
	
	
	

	1.  Structural Steel
	
	X
	1705.14.1
	 FORMCHECKBOX 

	     
	

	2.  Nonstructural Components
	
	X
	1705.14.2
	 FORMCHECKBOX 

	     
	

	3.  Designated Seismic Systems
	
	X
	1705.14.3
	 FORMCHECKBOX 

	     
	

	4.  Seismic Isolation Systems
	
	X
	1705.14.4
	 FORMCHECKBOX 

	     
	

	O. Sprayed Fire-Resistive Materials
	
	
	1705.15
	
	
	

	1.  Physical and visual tests
	
	X
	1705.15.1
	 FORMCHECKBOX 

	     
	

	2.  Structural Member Surface Conditions
	
	X
	1705.15.2
	 FORMCHECKBOX 

	     
	

	3.  Application
	
	X
	1705.15.3
	 FORMCHECKBOX 

	     
	

	4.  Thickness
	
	X
	1705.15.4
	 FORMCHECKBOX 

	     
	

	5.  Density
	
	X
	1705.15.5
	 FORMCHECKBOX 

	     
	

	6.  Bond Strength
	
	X
	1705.15.6
	 FORMCHECKBOX 

	     
	

	P. Intumescent Fire-Resistive Materials
	
	X
	1705.16
	 FORMCHECKBOX 

	     
	Performed in accordance with AWCI 12-B

	Q. Exterior Insulation and Finish Systems (EIFS)
	
	
	1705.17
	
	
	

	1.  Exterior Insulation and Finish Systems (EIFS)
	
	X
	1705.17
	 FORMCHECKBOX 

	     
	

	2.  Water Resistive Barrier Coating
	
	X
	1705.17.1
	 FORMCHECKBOX 

	     
	

	R. Fire-Resistant Penetrations and Joints
	
	
	1705.18
	
	
	

	1.  Penetration Firestops
	
	X
	1705.18.1
	 FORMCHECKBOX 

	     
	

	2.  Fire-resistant joint systems
	
	X
	1705.18.2
	 FORMCHECKBOX 

	     
	

	S. Testing for Smoke Control
	
	
	1705.19
	
	
	

	1.  Testing Scope
	
	X
	1705.19.1
	 FORMCHECKBOX 

	     
	

	2.  Qualifications
	
	X
	1705.19.2
	 FORMCHECKBOX 

	     
	

	T. Sealing of Mass Timber
	
	X
	1705.20
	 FORMCHECKBOX 

	     
	In accordance with BCNYS Section 703.7 where sealant or adhesive is applied to mass  timber building elements as designated in the approved construction documents.

	U. Additional Special  Inspections/Tests
	
	
	The registered design professional of record shall identify if additional tests and inspections defined by BC Section 1705.1.1 are required and provide specific requirements below. 

	1. 
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	
	 FORMCHECKBOX 

	     
	

	2. 
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	
	 FORMCHECKBOX 

	
	

	3. 
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	
	 FORMCHECKBOX 

	     
	

	4. 
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	
	 FORMCHECKBOX 

	     
	

	5. 
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	
	 FORMCHECKBOX 

	     
	

	6. 
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	
	 FORMCHECKBOX 

	     
	

	7. 
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	
	 FORMCHECKBOX 

	     
	

	8. 
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	
	 FORMCHECKBOX 

	     
	

	9. 
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	
	 FORMCHECKBOX 

	     
	

	10. 
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	
	 FORMCHECKBOX 

	     
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	


NOTES:

1. RDP to provide reference specification section detailing the requirements for inspections and/or tests and other clarifying notes, as necessary.

2. Commentary/Notes by DASNY are provided for information only and are not intended to provide complete details of the required tests and inspections.  Refer to the Building Code of New York State for complete and detailed requirements.
       2025 Building Code of New York State – Statement of Special Inspections (12/2025)                                                               Page 1 of 15

